## Cables
Cable Id | Tag | Type | From Location | To Location | Routing
Cable_Id_1 | =H3=HA4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA4=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_2 | =H3=HA4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA4=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_3 | =H3=HA4=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA4=BPA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_4 | =H3=HA4=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA4=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_5 | =H3=HA4=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA4=BPA2 | =L1=JL1+2 | /SECONDARY/BC134/BC135
Cable_Id_6 | =H3=HA5=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA5=BTA1 | =L1=JL2+2 | /SECONDARY/BC134/C132
Cable_Id_7 | =H3=HA5=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA5=BPA1 | =L1=JL2+2 | /SECONDARY/BC134/C132
Cable_Id_8 | =H3=HA5=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA5=BPA2 | =L1=JL1+1 | /SECONDARY
Cable_Id_9 | =H3=HA5=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA5=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_10 | =H3=KF1=GQB1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FT =H3=KF1=GQB1=BFA1 | =L1=JL1+2 | /SECONDARY/BC142/BC141/BC135
Cable_Id_11 | =H3=HA2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_12 | =H3=HA2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA2=QNB1 | =L1=JL3+1 | /C130/C131/C132/BC134/BC142
Cable_Id_13 | =H3=HA4=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA4=QNB1 | =L1=JL1+2 | /BC135/BC141/SECONDARY
Cable_Id_14 | =H3=HA4=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA4=QNB1 | =L1=JL1+1 | /BC135/BC141/SECONDARY
Cable_Id_15 | =H3=HA4=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=HA4=QNB1 | =L1=JL1+2 | /BC135/BC141/SECONDARY
Cable_Id_16 | =H3=HA5=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA5=QNB1 | =L1=JL2+2 | /C132/BC134/BC142/SECONDARY
Cable_Id_17 | =H3=HA5=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA5=QNB1 | =L1=JL2+1 | /C132/BC134/BC142/SECONDARY
Cable_Id_18 | =H3=HA2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA2=BTA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_19 | =H3=HA5=QNB1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | PY =H3=HA5=QNB1 | =L1=JL2+2 | /C132/BC134/BC142/SECONDARY
Cable_Id_20 | =H3=HA1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA1=BPC1 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_21 | =H3=HA7=BTA1.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA7=BTA1.3 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_22 | =H3=HA7=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA7=BTA1.2 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_23 | =H3=HA7=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA7=BTA1.1 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_24 | =H3=HA7=BTA1.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA7=BTA1.3 | TIT =H3=HA7=BTA1.3 | /SECONDARY
Cable_Id_25 | =H3=HA7=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA7=BTA1.2 | TIT =H3=HA7=BTA1.2 | /SECONDARY
Cable_Id_26 | =H3=HA7=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA7=BTA1.1 | TIT =H3=HA7=BTA1.1 | /SECONDARY
Cable_Id_27 | =H3=HA3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA3=BPC1 | =L1=JL3+2 | /C130/BC138/BC136
Cable_Id_28 | =H3=JF1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF1=BPA1.1 | =L1=JL1+1 | /BC135/BC136/SECONDARY
Cable_Id_29 | =H3=JF1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF1=BPA1.2 | =L1=JL1+1 | /BC135/BC136/SECONDARY
Cable_Id_30 | =H3=JF2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF2=BPA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_31 | =H3=JF2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF2=BPA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_32 | =H3=JF1=BPC1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JF1=BPC1.1 | =L1=JL2+1 | /C132/BC134/BC142/BC141/BC135/BC136/SECONDARY
Cable_Id_33 | =H3=JF1=BPC1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JF1=BPC1.2 | =L1=JL2+1 | /C132/BC134/BC142/BC141/BC135/BC136/SECONDARY
Cable_Id_34 | =H3=HC1=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =H3=HC1=BLA1 | =L1=JL1+2 | /BC135/BC136/SECONDARY
Cable_Id_35 | =H3=HC1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HC1=BPA1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/SECONDARY
Cable_Id_36 | =H3=HC1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HC1=BTA1.1 | =L1=JL2+1 | /C132/BC134/BC142/BC141/BC135/BC136/SECONDARY
Cable_Id_37 | =H3=HC1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HC1=BTA1.2 | =L1=JL2+1 | /C132/BC134/BC142/BC141/BC135/BC136/SECONDARY
Cable_Id_38 | =H3=HC1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HC1=BTA1.2 | TIT =H3=HC1=BTA1.2 | /SECONDARY
Cable_Id_39 | =H3=HC1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HC1=BTA1.1 | TIT =H3=HC1=BTA1.1 | /SECONDARY
Cable_Id_40 | =H3=HE1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HE1=BPA1 | =L1=JL1+1 | /SECONDARY
Cable_Id_41 | =H3=JF2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF2=BTA2.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_42 | =H3=JF2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF2=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_43 | =H3=JF2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF2=BTA1 | TIT =H3=JF2=BTA1 | /BC134/SECONDARY
Cable_Id_44 | =H3=JF2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF2=BTA2.1 | TIT =H3=JF2=BTA2.1 | /SECONDARY
Cable_Id_45 | =H3=JF2=BQC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | AIT =H3=JF2=BQC1 | =L1=JL1+2 | /BC135/BC134/C132
Cable_Id_46 | =H3=JF2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H3=JF2=BFB1 | =L1=JL1+2 | /BC135/BC134/C132
Cable_Id_47 | =H3=JF2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=JF2=BFA1 | =L1=JL1+1 | /BC135/BC134/C132
Cable_Id_48 | =H3=KC1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=KC1=BPC1 | =H3=KC1=UCA1X1-AI-X1-AI | /SECONDARY
Cable_Id_49 | =H3=JG2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JG2=BPA1.1 | =L1=JL3+1 | /C130/BC138/BC136/BC137/SECONDARY
Cable_Id_50 | =H3=JG2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JG2=BPA1.2 | =L1=JL3+1 | /C130/BC138/BC136/BC137/SECONDARY
Cable_Id_51 | =H3=JG2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JG2=BTA1 | =L1=JL3+2 | /C130/BC138/SECONDARY
Cable_Id_52 | =H3=JG2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JG2=BTA1 | TIT =H3=JG2=BTA1 | /SECONDARY/BC136/BC137/SECONDARY
Cable_Id_53 | =H3=JG2=BQC1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | UT =H3=JG2=BQC1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_54 | =H3=JG2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JG2=BPC1 | =L1=JL3+2 | /C130/C129/C128/SECONDARY
Cable_Id_55 | =H3=JG2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JG2=BPC2 | =L1=JL3+2 | /C130/BC138/BC136/BC137/SECONDARY
Cable_Id_56 | =H3=JG2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H3=JG2=BFB1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_57 | =H3=JG2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JG2=QNA1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_58 | =H3=JG2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=JG2=QNA1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_59 | =H3=JG1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JG1=BPA1.2 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_60 | =H3=JG1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JG1=BPA1.1 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_61 | =H3=JG1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JG1=BPC1 | =L1=JL3+2 | /C130/BC138/SECONDARY
Cable_Id_62 | =H3=JG1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=JG1=BFA1 | =L1=JL1+2 | /BC135/BC136/SECONDARY
Cable_Id_63 | =H3=JG1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JG1=BPA2 | =L1=JL3+2 | /C130/BC138/SECONDARY
Cable_Id_64 | =H3=JG1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JG1=BTA1 | =L1=JL3+2 | /C130/C129/C128/SECONDARY
Cable_Id_65 | =H3=JG1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JG1=BTA1 | TIT =H3=JG1=BTA1 | /SECONDARY
Cable_Id_66 | =H3=JF3=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF3=BTA1 | TIT =H3=JF3=BTA1 | /SECONDARY
Cable_Id_67 | =H3=JF3=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF3=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_68 | =H3=JF3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF3=BPA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_69 | =H3=JF3=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=JF3=BPA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/BC176/BC034/BC033/SECONDARY
Cable_Id_70 | =H3=JF3=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JF3=BPC2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/BC176/BC034/BC033/SECONDARY
Cable_Id_71 | =H3=JF3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=JF3=BPC1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_72 | =H3=JF3=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=JF3=BFA1 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_73 | =H3=JF4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF4=BTA1 | TIT =H3=JF4=BTA1 | /SECONDARY
Cable_Id_74 | =H3=JF4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF4=BTA2 | TIT =H3=JF4=BTA2 | /BC033/BC021/SECONDARY
Cable_Id_75 | =H3=JF4=BTA3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF4=BTA3 | TIT =H3=JF4=BTA3 | /BC033/BC021/SECONDARY
Cable_Id_76 | =H3=JF4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF4=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_77 | =H3=JF4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF4=BTA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/BC176/BC034/BC033/SECONDARY
Cable_Id_78 | =H3=JF4=BTA3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF4=BTA3 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/BC176/BC034/BC033/SECONDARY
Cable_Id_79 | =H3=JF4=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF4=QNA1 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_80 | =H3=JF4=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_81 | =H3=JF4=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_82 | =H3=JF4=QNA2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_83 | =H3=JF4=QNA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF4=QNA2 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_84 | =H3=JF4=QNA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_85 | =H3=JF2=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF2=QMA10 | =L1=JL2+2 | /C132/BC134
Cable_Id_86 | =H3=HC2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HC2=BPC1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_87 | =H3=HC2=BFA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=HC2=BFA3 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_88 | =H3=HC2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=HC2=BFA1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_89 | =H3=HC2=BFA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=HC2=BFA4 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_90 | =H3=HC2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HC2=BTA1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_91 | =H3=HC2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HC2=BTA1 | TIT =H3=HC2=BTA1 | /SECONDARY
Cable_Id_92 | =H3=HC2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=HC2=BFA2 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_93 | =H3=HC2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=HC2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_94 | =H3=HC2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HC2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_95 | =H3=HC2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HC2=QNB1 | =L1=JL3+1 | /C130/C131/C132/BC134/BC142
Cable_Id_96 | =H3=KF1=MAA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=KF1=MAA1=BPA1.1 | =L1=JL3+1 | /C130/C131/SECONDARY
Cable_Id_97 | =H3=KF1=MAA1=BPA1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=KF1=MAA1=BPA1.3 | =L1=JL3+1 | /C130/C131/SECONDARY
Cable_Id_98 | =H3=KF1=MAA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=KF1=MAA1=BPA1.2 | =L1=JL3+1 | /C130/C131/SECONDARY
Cable_Id_99 | =H3=KF1=PZA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | XI =H3=KF1=PZA1 | =L1=JL3+2 | /C130/BC138/SECONDARY
Cable_Id_100 | =H3=HA5=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA5=QMB1 | =L1=JL2+1 | /C132/BC134/BC142/SECONDARY
Cable_Id_101 | =H3=HA5=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA5=QMB1 | =L1=JL2+1 | /C132/BC134/BC142/SECONDARY
Cable_Id_102 | =H3=HA2=FLA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA2=FLA1 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_103 | =H3=HA2=FLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA2=FLA1 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_104 | =H3=HA7=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106//C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/BC138/BC136/BC137/SECONDARY
Cable_Id_105 | =H3=HA7=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106//C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/BC138/BC136/BC137/SECONDARY
Cable_Id_106 | =H3=JF2=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H3=JF2=BLB1 | =L1=JL2+2
Cable_Id_107 | =H3=JF1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H3=JF1=BLB1 | =L1=JL1+2
Cable_Id_108 | =H3=HC1=QMA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_109 | =H3=HC1=QMA4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_110 | =H3=HA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA1=BPA1.1 | =L1=JL2+1 | /C132/BC134/BC135/SECONDARY
Cable_Id_111 | =H3=JF1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF1=QMB1 | =L1=JL1+2 | /BC135/BC134/SECONDARY
Cable_Id_112 | =H3=JF1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF1=QMB1 | =L1=JL1+2 | /BC135/BC134/SECONDARY
Cable_Id_113 | =H3=HC2=QNB2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HC2=QNB2 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142/SECONDARY
Cable_Id_114 | =H3=HC2=QNB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HC2=QNB2 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142/SECONDARY
Cable_Id_115 | =H3=HA2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=HA2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_116 | =H3=HA5=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=HA5=QNB1 | =L1=JL2+2 | /C132/BC134/BC142/SECONDARY
Cable_Id_117 | =H3=HA4=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=HA4=QNB1 | =L1=JL1+2 | /BC135/BC141/SECONDARY
Cable_Id_118 | =H3=HC2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=HC2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_119 | =H3=JG2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=JG2=QNA1 | =L1=JL2+2 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_120 | =H3=JF4=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_121 | =H3=JF4=QNA2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_122 | =H3=JF3=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=JF3=BFA2 | =L5=JL3+1 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_123 | =H3=HA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HA1=QMB1 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_124 | =H3=HA1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HA1=QMB1 | =L1=JL1+1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_125 | =H3=HE1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=HE1=QMA1 | =L1=JL1+1 | /BC135/SECONDARY
Cable_Id_126 | =H3=HE1=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=HE1=QMA1 | =L1=JL1+1 | /BC135/SECONDARY
Cable_Id_127 | =H3=HC2=QNB2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=HC2=QNB2 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142/SECONDARY
Cable_Id_128 | =H3=JF2=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF2=QMA10 | =L1=JL2+2 | /C132/BC134
Cable_Id_129 | =H3=JG2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JG2=QNA1 | =L1=JL2+1 | /C132/BC134/BC142/BC141/BC135/BC136/BC137/SECONDARY
Cable_Id_130 | =H3=HC2=QNB2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=HC2=QNB2 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142/SECONDARY
Cable_Id_131 | =H3=HC1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =H3=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_132 | =H3=JF1=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF1=QMA10 | =L1=JL1+2 | /BC135/BC136/BC137/SECONDARY
Cable_Id_133 | =H3=JF1=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF1=QMA10 | =L1=JL1+2 | /BC135/BC136/BC137/SECONDARY
Cable_Id_134 | =H3=JF2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF2=BTA2.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_135 | =H3=JF2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF2=BTA2.2 | TIT =H3=JF2=BTA2.2 | /SECONDARY
Cable_Id_136 | =H3=JF2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=JF2=BTA2.3 | =L1=JL1+1 | /SECONDARY
Cable_Id_137 | =H3=JF2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=JF2=BTA2.3 | TIT =H3=JF2=BTA2.3 | /SECONDARY
Cable_Id_138 | =H3=JF2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF2=QNA1 | =L1=JL3+2 | /C130/C131/SECONDARY
Cable_Id_139 | =H3=JF2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H3=JF2=QNA1 | =L1=JL3+2 | /C130/C131/SECONDARY
Cable_Id_140 | =H3=JF2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H3=JF2=QNA1 | =L1=JL3+2 | /C130/C131/SECONDARY
Cable_Id_141 | =H3=JF2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=JF2=QNA1 | =L1=JL3+2 | /BC135/BC134/C132
Cable_Id_142 | =H3=JF2=QMA6=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H3=JF2=QMA6 | =L1=JL1+2 | /SECONDARY
Cable_Id_143 | =H3=HA4=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H3=HA4=BFA1 | =L1=JL1+2 | /C132/BC134/BC142/SECONDARY
Cable_Id_144 | =H3=SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=SJB6 | =L1=JL1+1 | /C130/BC138/BC137/SECONDARY
Cable_Id_145 | =H3=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=SJB4 | =L1=JL2+1 | /C130/C131/SECONDARY
Cable_Id_146 | =H3=KF1=SJB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=KF1=SJB2 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_147 | =H3=KF1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=KF1=SJB1 | =L1=JL3+1 | /C130/BC138/SECONDARY
Cable_Id_148 | =H3=KF1=SJB5=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=KF1=SJB3 | =L1=JL3+1 | /SECONDARY
Cable_Id_149 | =H3=SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H3=SJB5 | =L1=JL3+1 | /C130/C129/C128/SECONDARY
Cable_Id_150 | =H3=HC1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =H3=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_151 | =H3=LC1=XDC2=WGA3 | RE-2X(St)H TiMF 5x3x0.75mm² | =H3=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_152 | =H3=LC1=XDC2=WGA4 | RE-2X(St)H TiMF 5x3x0.75mm² | =H3=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_153 | =H3=LC1=XDC2=WGA5 | RE-2X(St)H TiMF 5x3x0.75mm² | =H3=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_154 | =H3=LC1=XDC2=WGA6 | RE-2X(St)H TiMF 5x3x0.75mm² | =H3=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_155 | =H4=LC1=XDC1=WGA1 | Li02YCHXSHX[BK] 18x4 x 0.50mm² | =H4=LC1=XDC1-XT | =H4=LC1=UCA1-125XT......130XT | /DFC003-1/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/C135/C136/C137
Cable_Id_156 | =H4=LC1=XDC2=WGA2 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H4=LC1=XDC2-SMX7/1 | =H4=LC1=UCA1-121 SMX7/1 | /DFC003-1/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/C135/C136/C137
Cable_Id_157 | =H4=LC1=XDC2=WGA1 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H4=LC1=XDC2-SMX7/2 | =H4=LC1=UCA1-122 SMX7/2 | /DFC003-1/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/C135/C136/C137
Cable_Id_158 | =H4=LC1=XDC1=WDB2 | HXSLCHXSHX 12 x 6mm² | =H4=LC1=UCA1-105XPA | =H4=LC1=XDC1-XPA | /DFB018-2/DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B112/B114/B124/B125
Cable_Id_159 | =H4=LC1=XDC1=WGA2 | RE-2X(St)H 1x3x0.75mm² | =H4=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_160 | =H4=LC1=XDC1=WGA3 | RE-2X(St)H 1x3x0.75mm² | =H4=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_161 | =H4=LC1=XDC1=WDB4 | HXSLCHXSHX 12 x 6mm² | =H4=LC1=UCA1-105XPM | =H4=LC1=XDC1-XPM | /DFB018-2/DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B112/B114/B124/B125
Cable_Id_162 | =H4=LC1=XDC2=WGA7 | RE-2X(St)H 1x3x0.75mm² | =H4=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_163 | =H4=LC1=XDC2=WGA8 | RE-2X(St)H 1x3x0.75mm² | =H4=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_164 | =H4=LC1=XDC1=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H4=LC1=XDC1-XG | /SECONDARY
Cable_Id_165 | =H4=LC1=XDC1=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H4=LC1=XDC1-XG | /SECONDARY
Cable_Id_166 | =H4=LC1=XDC2=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H4=LC1=XDC2-XG | /SECONDARY
Cable_Id_167 | =H4=LC1=XDC2=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H4=LC1=XDC2-XG | /SECONDARY
Cable_Id_168 | =H4=LC1=XDC1=BTA1=WGA1 | JZ-600 3G 1.5MM² | TSHL =H4=LC1=XDC1=BTA1 | =H4=LC1=XDC1-XPH | /SECONDARY
Cable_Id_169 | =H4=LC1=XDC2=BTA2=WGA1 | JZ-600 3G 1.5MM² | TSHL =H4=LC1=XDC2=BTA2 | =H4=LC1=XDC2-XPH | /SECONDARY
Cable_Id_170 | =H4=LC1=XDC1=WDB3 | HXSLCHXSHX 12 x 6mm² | =H4=LC1=XDC1-XPC | =H4=LC1=UCA1-105XPC | /DFB018-2/DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B112/B114/B124/B125
Cable_Id_171 | =H4=HA2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA2=BTA2.3 | TIT =H4=HA2=BTA2.3 | /SECONDARY
Cable_Id_172 | =H4=HA2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA2=BTA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_173 | =H4=HA2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA2=BTA2.2 | TIT =H4=HA2=BTA2.2 | /SECONDARY
Cable_Id_174 | =H4=HA2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA2=BTA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_175 | =H4=HA2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA2=BTA2.1 | TIT =H4=HA2=BTA2.1 | /SECONDARY
Cable_Id_176 | =H4=HA2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA2=BTA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_177 | =H4=HA2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA2=BTA1 | TIT =H4=HA2=BTA1 | /SECONDARY
Cable_Id_178 | =H4=HA2=BPA2.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA2=BPA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_179 | =H4=HA2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA2=BPA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_180 | =H4=HA2=BPA2.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA2=BPA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_181 | =H4=HA2=BPA2.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA2=BPA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_182 | =H4=HA2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=HA2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_183 | =H4=HA3=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA3=BTA1.2 | TIT =H4=HA3=BTA1.2 | /SECONDARY
Cable_Id_184 | =H4=HA3=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA3=BTA1.1 | TIT =H4=HA3=BTA1.1 | /SECONDARY
Cable_Id_185 | =H4=HA1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA1=BTA1.2 | TIT =H4=HA1=BTA1.2 | /SECONDARY
Cable_Id_186 | =H4=HA1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA1=BTA1.1 | TIT =H4=HA1=BTA1.1 | /SECONDARY
Cable_Id_187 | =H4=HA4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA4=BTA1 | TIT =H4=HA4=BTA1 | /SECONDARY
Cable_Id_188 | =H4=HA4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA4=BTA2 | TIT =H4=HA4=BTA2 | /SECONDARY
Cable_Id_189 | =H4=HA1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA1=BTA2 | TIT =H4=HA1=BTA2 | /SECONDARY
Cable_Id_190 | =H4=HA5=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA5=BTA1 | TIT =H4=HA5=BTA1 | /SECONDARY/BC156/BC148/SECONDARY
Cable_Id_191 | =H4=HA2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA2=BPC1 | =L1=JL3+1 | /C135/C134/C133/SECONDARY
Cable_Id_192 | =H4=HA2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA2=BPA3 | =L1=JL3+2 | /C135/C134/C133/SECONDARY
Cable_Id_193 | =H4=HA2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA2=BPC2 | =L1=JL3+2 | /C135/C134/C133/SECONDARY
Cable_Id_194 | =H4=HA3=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA3=BTA1.2 | =L1=JL3+1 | /C135/C134/C133/SECONDARY
Cable_Id_195 | =H4=HA3=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA3=BTA1.1 | =L1=JL3+1 | /C135/C134/C133/SECONDARY
Cable_Id_196 | =H4=HA3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA3=BPA1 | =L1=JL3+2 | /SECONDARY/BC151/BC150/BC152/C135
Cable_Id_197 | =H4=HA1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA1=BTA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_198 | =H4=HA1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA1=BTA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_199 | =H4=HA1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA1=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_200 | =H4=HA1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA1=BPC2 | =L1=JL1+1 | /SECONDARY/BC151/BC150/BC149
Cable_Id_201 | =H4=HA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA1=BPA1.2 | =L1=JL2+1 | /SECONDARY/BC149/BC148/C137
Cable_Id_202 | =H4=HA1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA1=BPA2 | =L1=JL2+2 | /SECONDARY/BC149/BC148/C137
Cable_Id_203 | =H4=HA4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA4=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_204 | =H4=HA4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA4=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_205 | =H4=HA4=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA4=BPA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_206 | =H4=HA4=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA4=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_207 | =H4=HA4=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA4=BPA2 | =L1=JL1+2 | /SECONDARY/BC148/BC149
Cable_Id_208 | =H4=HA5=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA5=BTA1 | =L1=JL2+2 | /SECONDARY/BC148/C137
Cable_Id_209 | =H4=HA5=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA5=BPA1 | =L1=JL2+2 | /SECONDARY/BC148/C137
Cable_Id_210 | =H4=HA5=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA5=BPA2 | =L1=JL1+1 | /SECONDARY
Cable_Id_211 | =H4=HA5=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA5=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_212 | =H4=KF1=GQB1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FT =H4=KF1=GQB1=BFA1 | =L1=JL1+2 | /SECONDARY/BC156/BC155/BC149
Cable_Id_213 | =H4=HA2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_214 | =H4=HA2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA2=QNB1 | =L1=JL3+1 | /C135/C136/C137/BC148/BC156
Cable_Id_215 | =H4=HA4=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA4=QNB1 | =L1=JL1+2 | /BC149/BC155/SECONDARY
Cable_Id_216 | =H4=HA4=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA4=QNB1 | =L1=JL1+1 | /BC149/BC155/SECONDARY
Cable_Id_217 | =H4=HA4=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=HA4=QNB1 | =L1=JL1+2 | /BC149/BC155/SECONDARY
Cable_Id_218 | =H4=HA5=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA5=QNB1 | =L1=JL2+2 | /C137/BC148/BC156/SECONDARY
Cable_Id_219 | =H4=HA5=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA5=QNB1 | =L1=JL2+1 | /C137/BC148/BC156/SECONDARY
Cable_Id_220 | =H4=HA2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA2=BTA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_221 | =H4=HA5=QNB1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | PY =H4=HA5=QNB1 | =L1=JL2+2 | /C137/BC148/BC156/SECONDARY
Cable_Id_222 | =H4=HA1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA1=BPC1 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_223 | =H4=HA7=BTA1.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA7=BTA1.3 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_224 | =H4=HA7=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA7=BTA1.2 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_225 | =H4=HA7=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HA7=BTA1.1 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_226 | =H4=HA7=BTA1.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA7=BTA1.3 | TIT =H4=HA7=BTA1.3 | /SECONDARY
Cable_Id_227 | =H4=HA7=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA7=BTA1.2 | TIT =H4=HA7=BTA1.2 | /SECONDARY
Cable_Id_228 | =H4=HA7=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HA7=BTA1.1 | TIT =H4=HA7=BTA1.1 | /SECONDARY
Cable_Id_229 | =H4=HA3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HA3=BPC1 | =L1=JL3+2 | /C135/BC152/BC150
Cable_Id_230 | =H4=JF1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF1=BPA1.1 | =L1=JL1+1 | /BC149/BC150/SECONDARY
Cable_Id_231 | =H4=JF1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF1=BPA1.2 | =L1=JL1+1 | /BC149/BC150/SECONDARY
Cable_Id_232 | =H4=JF2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF2=BPA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_233 | =H4=JF2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF2=BPA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_234 | =H4=JF1=BPC1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JF1=BPC1.1 | =L1=JL2+1 | /C137/BC148/BC156/BC155/BC149/BC150/SECONDARY
Cable_Id_235 | =H4=JF1=BPC1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JF1=BPC1.2 | =L1=JL2+1 | /C137/BC148/BC156/BC155/BC149/BC150/SECONDARY
Cable_Id_236 | =H4=HC1=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =H4=HC1=BLA1 | =L1=JL1+2 | /BC149/BC150/SECONDARY
Cable_Id_237 | =H4=HC1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HC1=BPA1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/SECONDARY
Cable_Id_238 | =H4=HC1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HC1=BTA1.1 | =L1=JL2+1 | /C137/BC148/BC156/BC155/BC149/BC150/SECONDARY
Cable_Id_239 | =H4=HC1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HC1=BTA1.2 | =L1=JL2+1 | /C137/BC148/BC156/BC155/BC149/BC150/SECONDARY
Cable_Id_240 | =H4=HC1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HC1=BTA1.2 | TIT =H4=HC1=BTA1.2 | /SECONDARY
Cable_Id_241 | =H4=HC1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HC1=BTA1.1 | TIT =H4=HC1=BTA1.1 | /SECONDARY
Cable_Id_242 | =H4=HE1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HE1=BPA1 | =L1=JL1+1 | /SECONDARY
Cable_Id_243 | =H4=JF2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF2=BTA2.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_244 | =H4=JF2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF2=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_245 | =H4=JF2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF2=BTA1 | TIT =H4=JF2=BTA1 | /BC148/SECONDARY
Cable_Id_246 | =H4=JF2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF2=BTA2.1 | TIT =H4=JF2=BTA2.1 | /SECONDARY
Cable_Id_247 | =H4=JF2=BQC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | AIT =H4=JF2=BQC1 | =L1=JL1+2 | /BC149/BC148/C137
Cable_Id_248 | =H4=JF2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H4=JF2=BFB1 | =L1=JL1+2 | /BC149/BC148/C137
Cable_Id_249 | =H4=JF2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=JF2=BFA1 | =L1=JL1+1 | /BC149/BC148/C137
Cable_Id_250 | =H4=KC1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=KC1=BPC1 | =H4=KC1=UCA1X1-AI-X1-AI | /SECONDARY
Cable_Id_251 | =H4=JG2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JG2=BPA1.1 | =L1=JL3+1 | /C135/BC152/BC150/BC151/SECONDARY
Cable_Id_252 | =H4=JG2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JG2=BPA1.2 | =L1=JL3+1 | /C135/BC152/BC150/BC151/SECONDARY
Cable_Id_253 | =H4=JG2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JG2=BTA1 | =L1=JL3+2 | /C135/BC152/SECONDARY
Cable_Id_254 | =H4=JG2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JG2=BTA1 | TIT =H4=JG2=BTA1 | /SECONDARY/BC150/BC151/SECONDARY
Cable_Id_255 | =H4=JG2=BQC1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | UT =H4=JG2=BQC1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_256 | =H4=JG2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JG2=BPC1 | =L1=JL3+2 | /C135/C134/C133/SECONDARY
Cable_Id_257 | =H4=JG2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JG2=BPC2 | =L1=JL3+2 | /C135/BC152/BC150/BC151/SECONDARY
Cable_Id_258 | =H4=JG2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H4=JG2=BFB1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_259 | =H4=JG2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JG2=QNA1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_260 | =H4=JG2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=JG2=QNA1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_261 | =H4=JG1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JG1=BPA1.2 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_262 | =H4=JG1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JG1=BPA1.1 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_263 | =H4=JG1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JG1=BPC1 | =L1=JL3+2 | /C135/BC152/SECONDARY
Cable_Id_264 | =H4=JG1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=JG1=BFA1 | =L1=JL1+2 | /BC149/BC150/SECONDARY
Cable_Id_265 | =H4=JG1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JG1=BPA2 | =L1=JL3+2 | /C135/BC152/SECONDARY
Cable_Id_266 | =H4=JG1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JG1=BTA1 | =L1=JL3+2 | /C135/C134/C133/SECONDARY
Cable_Id_267 | =H4=JG1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JG1=BTA1 | TIT =H4=JG1=BTA1 | /SECONDARY
Cable_Id_268 | =H4=JF3=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF3=BTA1 | TIT =H4=JF3=BTA1 | /SECONDARY
Cable_Id_269 | =H4=JF3=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF3=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_270 | =H4=JF3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF3=BPA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_271 | =H4=JF3=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=JF3=BPA2 | =L5=JL3+2 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_272 | =H4=JF3=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JF3=BPC2 | =L5=JL3+2 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_273 | =H4=JF3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=JF3=BPC1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_274 | =H4=JF3=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=JF3=BFA1 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_275 | =H4=JF4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF4=BTA1 | TIT =H4=JF4=BTA1 | /SECONDARY
Cable_Id_276 | =H4=JF4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF4=BTA2 | TIT =H4=JF4=BTA2 | /SECONDARY/BC035/BC034/BC033
Cable_Id_277 | =H4=JF4=BTA3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF4=BTA3 | TIT =H4=JF4=BTA3 | /SECONDARY/BC035/BC034/BC033
Cable_Id_278 | =H4=JF4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF4=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_279 | =H4=JF4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF4=BTA2 | =L5=JL3+2 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_280 | =H4=JF4=BTA3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF4=BTA3 | =L5=JL3+2 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_281 | =H4=JF4=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF4=QNA1 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_282 | =H4=JF4=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_283 | =H4=JF4=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_284 | =H4=JF4=QNA2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_285 | =H4=JF4=QNA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF4=QNA2 | =L5=JL3+1 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_286 | =H4=JF4=QNA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_287 | =H4=JF2=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF2=QMA10 | =L1=JL2+2 | /C137/BC148
Cable_Id_288 | =H4=HC2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H4=HC2=BPC1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_289 | =H4=HC2=BFA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=HC2=BFA3 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_290 | =H4=HC2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=HC2=BFA1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_291 | =H4=HC2=BFA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=HC2=BFA4 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_292 | =H4=HC2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=HC2=BTA1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_293 | =H4=HC2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=HC2=BTA1 | TIT =H4=HC2=BTA1 | /SECONDARY
Cable_Id_294 | =H4=HC2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=HC2=BFA2 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_295 | =H4=HC2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=HC2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_296 | =H4=HC2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HC2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_297 | =H4=HC2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HC2=QNB1 | =L1=JL3+1 | /C135/C136/C137/BC148/BC156
Cable_Id_298 | =H4=KF1=MAA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=KF1=MAA1=BPA1.1 | =L1=JL3+1 | /C135/C136/SECONDARY
Cable_Id_299 | =H4=KF1=MAA1=BPA1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=KF1=MAA1=BPA1.3 | =L1=JL3+1 | /C135/C136/SECONDARY
Cable_Id_300 | =H4=KF1=MAA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=KF1=MAA1=BPA1.2 | =L1=JL3+1 | /C135/C136/SECONDARY
Cable_Id_301 | =H4=KF1=PZA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | XI =H4=KF1=PZA1 | =L1=JL3+2 | /C135/BC152/SECONDARY
Cable_Id_302 | =H4=HA5=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA5=QMB1 | =L1=JL2+1 | /C137/BC148/BC156/SECONDARY
Cable_Id_303 | =H4=HA5=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA5=QMB1 | =L1=JL2+1 | /C137/BC148/BC156/SECONDARY
Cable_Id_304 | =H4=HA2=FLA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA2=FLA1 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_305 | =H4=HA2=FLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA2=FLA1 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_306 | =H4=HA7=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/BC152/BC150/BC151/SECONDARY
Cable_Id_307 | =H4=HA7=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/BC152/BC150/BC151/SECONDARY
Cable_Id_308 | =H4=JF2=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H4=JF2=BLB1 | =L1=JL2+2
Cable_Id_309 | =H4=JF1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H4=JF1=BLB1 | =L1=JL1+2
Cable_Id_310 | =H4=HC1=QMA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_311 | =H4=HC1=QMA4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_312 | =H4=HA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H4=HA1=BPA1.1 | =L1=JL2+1 | /C137/BC148/BC149/SECONDARY
Cable_Id_313 | =H4=JF1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF1=QMB1 | =L1=JL1+2 | /BC149/BC148/SECONDARY
Cable_Id_314 | =H4=JF1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF1=QMB1 | =L1=JL1+2 | /BC149/BC148/SECONDARY
Cable_Id_315 | =H4=HC2=QNB2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HC2=QNB2 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156/SECONDARY
Cable_Id_316 | =H4=HC2=QNB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HC2=QNB2 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156/SECONDARY
Cable_Id_317 | =H4=HA2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=HA2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_318 | =H4=HA5=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=HA5=QNB1 | =L1=JL2+2 | /C137/BC148/BC156/SECONDARY
Cable_Id_319 | =H4=HA4=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=HA4=QNB1 | =L1=JL1+2 | /BC149/BC155/SECONDARY
Cable_Id_320 | =H4=HC2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=HC2=QNB1 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156
Cable_Id_321 | =H4=JG2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=JG2=QNA1 | =L1=JL2+2 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_322 | =H4=JF4=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_323 | =H4=JF4=QNA2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/BC180/BC026/BC023-1/SECONDARY
Cable_Id_324 | =H4=JF3=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=JF3=BFA2 | =L5=JL3+1 | /BC019-1/C138-1/C107-5/BC176/BC034/BC033/SECONDARY
Cable_Id_325 | =H4=HA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HA1=QMB1 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_326 | =H4=HA1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HA1=QMB1 | =L1=JL1+1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_327 | =H4=HE1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=HE1=QMA1 | =L1=JL1+1 | /BC149/SECONDARY
Cable_Id_328 | =H4=HE1=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=HE1=QMA1 | =L1=JL1+1 | /BC149/SECONDARY
Cable_Id_329 | =H4=HC2=QNB2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=HC2=QNB2 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156/SECONDARY
Cable_Id_330 | =H4=JF2=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF2=QMA10 | =L1=JL2+2 | /C137/BC148
Cable_Id_331 | =H4=JG2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JG2=QNA1 | =L1=JL2+1 | /C137/BC148/BC156/BC155/BC149/BC150/BC151/SECONDARY
Cable_Id_332 | =H4=HC2=QNB2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=HC2=QNB2 | =L1=JL3+2 | /C135/C136/C137/BC148/BC156/SECONDARY
Cable_Id_333 | =H4=HC1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =H4=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_334 | =H4=JF1=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF1=QMA10 | =L1=JL1+2 | /BC149/BC150/BC151/SECONDARY
Cable_Id_335 | =H4=JF1=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF1=QMA10 | =L1=JL1+2 | /BC149/BC150/BC151/SECONDARY
Cable_Id_336 | =H4=JF2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF2=BTA2.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_337 | =H4=JF2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF2=BTA2.2 | TIT =H4=JF2=BTA2.2 | /SECONDARY
Cable_Id_338 | =H4=JF2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H4=JF2=BTA2.3 | =L1=JL1+1 | /SECONDARY
Cable_Id_339 | =H4=JF2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H4=JF2=BTA2.3 | TIT =H4=JF2=BTA2.3 | /SECONDARY
Cable_Id_340 | =H4=JF2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF2=QNA1 | =L1=JL3+2 | /C135/C136/SECONDARY
Cable_Id_341 | =H4=JF2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H4=JF2=QNA1 | =L1=JL3+2 | /C135/C136/SECONDARY
Cable_Id_342 | =H4=JF2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H4=JF2=QNA1 | =L1=JL3+2 | /C135/C136/SECONDARY
Cable_Id_343 | =H4=JF2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H4=JF2=QNA1 | =L1=JL3+2 | /BC149/BC148/C137
Cable_Id_344 | =H4=JF2=QMA6=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H4=JF2=QMA6 | =L1=JL1+2 | /SECONDARY
Cable_Id_345 | =H4=HA4=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H4=HA4=BFA1 | =L1=JL1+2 | /C137/BC148/BC156/SECONDARY
Cable_Id_346 | =H4=SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=SJB6 | =L1=JL1+1 | /C135/BC152/BC151/SECONDARY
Cable_Id_347 | =H4=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=SJB4 | =L1=JL2+1 | /C135/C136/SECONDARY
Cable_Id_348 | =H4=KF1=SJB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=KF1=SJB2 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_349 | =H4=KF1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=KF1=SJB1 | =L1=JL3+1 | /C135/BC152/SECONDARY
Cable_Id_350 | =H4=KF1=SJB5=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=KF1=SJB3 | =L1=JL3+1 | /SECONDARY
Cable_Id_351 | =H4=SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H4=SJB5 | =L1=JL3+1 | /C135/C134/C133/SECONDARY
Cable_Id_352 | =H4=HC1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =H4=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_353 | =H4=LC1=XDC2=WGA3 | RE-2X(St)H TiMF 5x3x0.75mm² | =H4=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_354 | =H4=LC1=XDC2=WGA4 | RE-2X(St)H TiMF 5x3x0.75mm² | =H4=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_355 | =H4=LC1=XDC2=WGA5 | RE-2X(St)H TiMF 5x3x0.75mm² | =H4=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_356 | =H4=LC1=XDC2=WGA6 | RE-2X(St)H TiMF 5x3x0.75mm² | =H4=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_357 | =P1=LA2=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA2=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C108/C123/SECONDARY
Cable_Id_358 | =P1=LA2=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA2=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C108/C123/SECONDARY
Cable_Id_359 | =P1=LA2=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA2=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C108/C123/SECONDARY
Cable_Id_360 | =P1=LA2=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA2=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C108/C123/SECONDARY
Cable_Id_361 | =P1=LA3=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA3=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C128/SECONDARY
Cable_Id_362 | =P1=LA3=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA3=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C128/SECONDARY
Cable_Id_363 | =P1=LA3=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA3=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C128/SECONDARY
Cable_Id_364 | =P1=LA3=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA3=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C128/SECONDARY
Cable_Id_365 | =P1=LA4=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA4=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C114/C133/SECONDARY
Cable_Id_366 | =P1=LA4=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA4=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C114/C133/SECONDARY
Cable_Id_367 | =P1=LA4=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA4=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C114/C133/SECONDARY
Cable_Id_368 | =P1=LA4=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA4=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C143-1/C143-2/C143-3/C143-4/C143-5/BC180/BC181/C111/C114/C133/SECONDARY
Cable_Id_369 | =L1=K3=JK3=WDB1 | N2XH-Flex 0.6/1 kV 5G35mm² | =K1=JK3+1-UPS1.XD0 | LV ROOM CLIENTTBA-X201 | /DFBC001-1/DFB020/B001/BC174/LV_ROOM_CLIENT
Cable_Id_370 | =L1=K3=JK3=WDB2 | N2XH-Flex 0.6/1 kV 5G35mm² | =K1=JK3+1-UPS2.XD0 | LV ROOM CLIENTTBA-X202 | /DFBC001-1/DFB020/B001/BC174/LV_ROOM_CLIENT
Cable_Id_371 | =H7=HE1=UCA3=WDB1 | N2XH-Flex 0.6/1 kV 4G120mm² | =H7=HE1=UCA2-QB1 | =H7=HE1=UCA3-X1 | /B142/BC027
Cable_Id_372 | =P1=LC1=WGA1 | RE-2X(St)H PiMF 4x2x0.75mm² | =P1=LC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC001/DFC005/DFC006/BC001/BC002
Cable_Id_373 | =L3=JL1+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-HPU3.XD2 | =L3=JL1+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/BC138/BC136/BC135
Cable_Id_374 | =F2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =F2=BFA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_375 | =F2=QC2=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =F2=QC2=BLA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172/BC164/SECONDARY
Cable_Id_376 | =F2=QC2=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC2=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172
Cable_Id_377 | =F2=KF1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF1=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_378 | =F2=KF2=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF2=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_379 | =F2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=BPA3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_380 | =F2=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=BPA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC169/SECONDARY
Cable_Id_381 | =P1=LA5=PZA3=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA5=PZA3 | =P1=LA5=XDC1-FDO | /SECONDARY/BC167/C004/BC003/BC004/BC160-2/BC161/BC162/SECONDARY
Cable_Id_382 | =F2=QC3=BLB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC3=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/SECONDARY
Cable_Id_383 | =F2=KF1=GQA1=XDC2=WGA2 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_384 | =F2=KF2=GQA1=XDC2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_385 | =F2=QC1=QMA11=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC1=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_386 | =F2=QC1=QMA11=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC1=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_387 | =F2=QC1=QMA11=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =F2=QC1=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_388 | =F2=QC2=QMA11=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=JF1=QMA2 |  | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_389 | =F2=QC2=QMA11=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=JF2=QMA2 |  | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_390 | =F2=QC2=QMA11=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=JF1=QMA2 |  | /BC166-2/BC160-1/C145/C144/BC177/BC178/SECONDARY
Cable_Id_391 | =F2=QC2=QMA11=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=JF2=QMA2 |  | /BC166-2/BC160-1/C145/C144/BC177/BC178/SECONDARY
Cable_Id_392 | =F2=QC2=QMA11=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =F2=QC2=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/SECONDARY
Cable_Id_393 | =F2=QC3=QMA11=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC3=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/BC179/SECONDARY
Cable_Id_394 | =F2=QC3=QMA11=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC3=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/BC179/SECONDARY
Cable_Id_395 | =F2=QC3=QMA11=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =F2=QC3=QMA11 | =L5=JL2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/BC179/SECONDARY
Cable_Id_396 | =E1=JA1=UCA1=WGA1 | RE-2X(St)H PiMF 4x2x0.75mm² | =E1=JA1=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/BC167/SECONDARY
Cable_Id_397 | =E1=JA1=UCA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =E1=JA1=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/BC167/SECONDARY
Cable_Id_398 | =E1=JA2=UCA1=WGA1 | RE-2X(St)H PiMF 4x2x0.75mm² | =E1=JA2=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C005/BC168/SECONDARY
Cable_Id_399 | =E1=JA2=UCA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =E1=JA2=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C005/BC168/SECONDARY
Cable_Id_400 | =F1=HD1=HQB1=UCA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | =F1=HD1=HQB1=UCA1 | =L5=JL1 | /SECONDARY
Cable_Id_401 | =F1=HD1=HQB1=UCA1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =F1=HD1=HQB1=UCA1 | =L5=JL1 | /SECONDARY
Cable_Id_402 | =F1=HD1=HQB1=UCA1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =F1=HD1=HQB1=UCA1 | =L5=JL1 | /SECONDARY
Cable_Id_403 | =F2=EBB1=UCA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | =F2=EBB1=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C005/BC168/SECONDARY
Cable_Id_404 | =F2=EBB1=UCA1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =F2=EBB1=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C005/BC168/SECONDARY
Cable_Id_405 | =F2=EBB1=UCA1=WGA3 | RE-2X(St)H PiMF 4x2x0.75mm² | =F2=EBB1=UCA1 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C005/BC168/SECONDARY
Cable_Id_406 | =F2=QC2=QMA11=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC2=QMA11 | =L5=JL2 | /SECONDARY/BC178
Cable_Id_407 | =F2=QC2=QMA11=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC2=QMA11 | =L5=JL2 | /SECONDARY/BC179
Cable_Id_408 | =H1=JF1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H1=JF1=QMA1 | =L1=JL1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_409 | =H1=JF1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H1=JF1=QMA1 | =L1=JL1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_410 | =H1=JF1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JF1=QMA1 | =L1=JL1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_411 | =H1=JF2=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JF2=BFA1 | =L1=JL1 | /BC107/BC106/SECONDARY
Cable_Id_412 | =H1=JF3=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JF3=BFA1 | =L5=JL3 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_413 | =H1=JF3=BFA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JF3=BFA2 | =L5=JL3 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC020
Cable_Id_414 | =H1=JG1=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JG1=BFA1 | =L1=JL1 | /BC107/BC108/BC110/SECONDARY
Cable_Id_415 | =H1=JG1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H1=JG1=QMA1 | =L1=JL3 | /C120/BC110/BC109/SECONDARY
Cable_Id_416 | =H1=JG1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H1=JG1=QMA1 | =L1=JL3 | /C120/BC110/BC109/SECONDARY
Cable_Id_417 | =H1=JG1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H1=JG1=QMA1 | =L1=JL3 | /C120/BC110/BC109/SECONDARY
Cable_Id_418 | =H1=KC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=KC1=UCA1 | =L1=JL2 | /C122/BC106/SECONDARY
Cable_Id_419 | =H1=KC1=UCA1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=KC1=UCA1 | =L1=JL2 | /C122/BC106/SECONDARY
Cable_Id_420 | =H1=KC1=UCA1=WGA3 | RE-2X(St)H PiMF 4x2x0.75mm² | =H1=KC1=UCA1 | =L1=JL2 | /C122/BC106/SECONDARY
Cable_Id_421 | =H1=KC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=KC1=UCA1 | =L1=JL2 | /C122/BC106/SECONDARY
Cable_Id_422 | =H1=KF1=TAA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=KF1=TAA1 | =H1=KF1=TAC1 | /BC022-2/BC022-1/BC025/C143-3/BC175/BC030/BC020
Cable_Id_423 | =H1=KF1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_424 | =H1=KF1=TAC1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_425 | =H1=KF1=TAC1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_426 | =H1=KF1=TAC1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_427 | =H1=KF1=TAC1=WGA5 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_428 | =H1=KF1=TAC1=WGA6 | RE-2X(St)H PiMF 4x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_429 | =H1=KF1=TAC1=WGA7 | RE-2X(St)H PiMF 4x2x0.75mm² | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_430 | =H1=KF1=TAC1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H1=KF1=TAC1 | =L1=LC1 | /DFBC002-1/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_431 | =H1=LC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H1=LC1=UCA1 | =L1=LC1 | /DFC015
Cable_Id_432 | =H1=LC1=UCA1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H1=LC1=UCA1 | =L1=LC1 | /DFC015
Cable_Id_433 | =H1=LC1=UCA1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=LC1=UCA1 | =L1=LC1 | /DFC015
Cable_Id_434 | =H1=LC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H1=LC1=UCA1 | =L1=LC1 | /DFC015
Cable_Id_435 | =H1=LC1=UCA1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H1=LC1=UCA1 | =L6=LC1 | /DFC013/DFC014/C001/C101/C102/C118/C119/C120/C121/C122
Cable_Id_436 | =H1=LC1=UCA1=WGB2 | CAT.6A S/FTP 4x2xAWG23 | =H1=LC1=UCA1 | =L1=LC1 | /DFC015
Cable_Id_437 | =H5=HE1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H5=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_438 | =H5=HE1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H5=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_439 | =H6=HE1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H6=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_440 | =H6=HE1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H6=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_441 | =H7=HE1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H7=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/C140/SECONDARY
Cable_Id_442 | =H7=HE1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H7=HE1=UCA2 | =L5=JL3 | /BC019-2/C138-3/C139/C140/C140/SECONDARY
Cable_Id_443 | =H9=JG1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QMA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_444 | =H9=JG1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QMA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_445 | =H9=JG1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG1=QMA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_446 | =H9=JG1=QMA2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/SECONDARY
Cable_Id_447 | =H9=JG1=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/SECONDARY
Cable_Id_448 | =H9=JG1=QMA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/SECONDARY
Cable_Id_449 | =H9=JG1=QNA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QNA1 | =L5=JL1 | /BC011/C116/BC012/SECONDARY
Cable_Id_450 | =H9=JG1=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG1=QNA1 | =L5=JL1 | /BC011/C116/BC012/SECONDARY
Cable_Id_451 | =H9=JG1=QNA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG1=QNA1 | =L5=JL1 | /BC011/C116/BC012/SECONDARY
Cable_Id_452 | =H9=JG2=BFA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG2=BFA2 | =L5=JL3 | /BC019-2/C138-3
Cable_Id_453 | =H9=JG2=QNA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG2=QNA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_454 | =H9=JG2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG2=QNA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_455 | =H9=JG2=QNA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG2=QNA1 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_456 | =H9=JG2=QNA2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG2=QNA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_457 | =H9=JG2=QNA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=JG2=QNA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_458 | =H9=JG2=QNA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=JG2=QNA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_459 | =H9=KF1=GPB1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H9=KF1=GPB1=TAC1 | =K1=JK1+6 | /DFC012/DFC010/DFC009/DFC008/DFC007
Cable_Id_460 | =H9=KF1=GPB1=TAC1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H9=KF1=GPB1=TAC1 | =K1=JK1+6 | /DFC012/DFC010/DFC009/DFC008/DFC007
Cable_Id_461 | =H9=KF1=GPB1=TAC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF1=GPB1=TAC1 | =K1=JK1 | /DFC012/DFC010/DFC009
Cable_Id_462 | =H9=KF1=QMA2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_463 | =H9=KF1=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_464 | =H9=KF1=QMA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF1=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_465 | =H9=KF2=GPB1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H9=KF2=GPB1=TAC1 | =K1=JK1+6 | /DFC010/DFC009/DFC008
Cable_Id_466 | =H9=KF2=GPB1=TAC1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H9=KF2=GPB1=TAC1 | =K1=JK1+6 | /DFC010/DFC009/DFC008
Cable_Id_467 | =H9=KF2=GPB1=TAC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF2=GPB1=TAC1 | =H9=KF1=GPB1=TAC1 | /DFC010/DFC009/DFC008
Cable_Id_468 | =H9=KF2=QMA2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF2=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/SECONDARY
Cable_Id_469 | =H9=KF2=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF2=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/SECONDARY
Cable_Id_470 | =H9=KF2=QMA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF2=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/BC017/SECONDARY
Cable_Id_471 | =H9=KF3=GPB1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H9=KF3=GPB1=TAC1 | =K1=JK1+6 | /DFC010/DFC009
Cable_Id_472 | =H9=KF3=GPB1=TAC1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H9=KF3=GPB1=TAC1 | =K1=JK1+6 | /DFC010/DFC009
Cable_Id_473 | =H9=KF3=GPB1=TAC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF3=GPB1=TAC1 | =H9=KF2=GPB1=TAC1 | /DFC010/DFC009
Cable_Id_474 | =H9=KF3=QMA2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF3=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_475 | =H9=KF3=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF3=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_476 | =H9=KF3=QMA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H9=KF3=QMA2 | =L5=JL1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_477 | =K1=JK1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =K1=JK1 | =L6=LC1 | /DFC007/DFC008/DFC009/DFC010/DFC012
Cable_Id_478 | =K1=JK1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =K1=JK1 | =L6=LC1 | /DFC007/DFC008/DFC009/DFC010/DFC012
Cable_Id_479 | =K1=JK1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =K1=JK1 | =K1=JK3 | /DFBC001-1/DFC006/DFC005/DFC001/DFC002/DFC004-1/DFC004-2
Cable_Id_480 | =K1=JK2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =K1=JK2 | =H9=KF3=GPB1=TAC1 | /DFC011/DFC004-1/DFC004-2/DFC010/DFC009
Cable_Id_481 | =K1=JK3=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =K1=JK3 | =K1=JK2 | /DFC004-2/DFC002/DFC001/DFC005/DFC006/DFBC001-1
Cable_Id_482 | =L1=JL1+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L1=JL1 | =L1=JL1 | /BC107
Cable_Id_483 | =L1=JL1+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L1=JL1 | =L1=JL1 | /BC107
Cable_Id_484 | =L1=JL1+1=WHA1 | 4G 62.5/125μm OM1 | =L1=JL1 | =L1=LC1 | /DFBC002-1/DFC005/DFC006/C001/C101/C102/C118/C119/BC110/BC108/BC107
Cable_Id_485 | =L1=JL2+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L1=JL2 | =L1=JL2 | /INTERNAL
Cable_Id_486 | =L1=JL2+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L1=JL2 | =L1=JL2 | /INTERNAL
Cable_Id_487 | =L1=JL2+1=WHA1 | 4G 62.5/125μm OM1 | =L1=JL2 | =L1=JL1 | /BC107/BC106/C122
Cable_Id_488 | =L1=JL3+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L1=JL3 | =L1=JL3 | /INTERNAL
Cable_Id_489 | =L1=JL3+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L1=JL3 | =L1=JL3 | /INTERNAL
Cable_Id_490 | =L1=JL3+1=WHA1 | 4G 62.5/125μm OM1 | =L1=JL2 | =L1=JL3 | /C122/C121/C120
Cable_Id_491 | =L1=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | =L1=LC1 | /DFBC002-1/DFC005/DFC006/DFC014/DFC013
Cable_Id_492 | =L1=LC1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | =L1=LC1 | /DFBC002-1/DFC005/DFC006/DFC014/DFC013
Cable_Id_493 | =L1=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L1=LC1 | =L6=LC1 | /DFBC002-1/DFC005/DFC006/DFC014/DFC013
Cable_Id_494 | =L1=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | =L1=LC1 | /DFBC002-1/DFC005/DFC006/DFC014/DFC013
Cable_Id_495 | =L1=LC1=WHA1 | 4G 62.5/125μm OM1 | =L1=LC1 | =L1=JL3 | /DFBC002-1/DFC005/DFC006/C001/C101/C102/C118/C119/C120
Cable_Id_496 | =L2=JL1+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L2=JL1 | =L2=JL1 | /BC121
Cable_Id_497 | =L2=JL1+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L2=JL1 | =L2=JL1 | /BC121
Cable_Id_498 | =L2=JL2+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L2=JL2 | =L2=JL2 | /INTERNAL
Cable_Id_499 | =L2=JL2+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L2=JL2 | =L2=JL2 | /INTERNAL
Cable_Id_500 | =L2=JL3+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L2=JL3 | =L2=JL3 | /INTERNAL
Cable_Id_501 | =L2=JL3+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L2=JL3 | =L2=JL3 | /INTERNAL
Cable_Id_502 | =L2=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =L2=LC1 | =L6=LC1 | /DFBC002-2/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_503 | =L2=LC1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =L2=LC1 | =L6=LC1 | /DFBC002-2/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_504 | =L2=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L2=LC1 | =L6=LC1 | /DFBC002-2/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_505 | =L2=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L2=LC1 | =L6=LC1 | /DFBC002-2/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_506 | =L3=JL1+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L3=JL1 | =L3=JL1 | /BC135
Cable_Id_507 | =L3=JL1+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L3=JL1 | =L3=JL1 | /BC135
Cable_Id_508 | =L3=JL2+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L3=JL2 | =L3=JL2 | /INTERNAL
Cable_Id_509 | =L3=JL2+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L3=JL2 | =L3=JL2 | /INTERNAL
Cable_Id_510 | =L3=JL3+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L3=JL3 | =L3=JL3 | /INTERNAL
Cable_Id_511 | =L3=JL3+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L3=JL3 | =L3=JL3 | /INTERNAL
Cable_Id_512 | =L3=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =L3=LC1 | =L6=LC1 | /DFBC003-1/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_513 | =L3=LC1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =L3=LC1 | =L6=LC1 | /DFBC003-1/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_514 | =L3=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L3=LC1 | =L6=LC1 | /DFBC003-1/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_515 | =L3=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L3=LC1 | =L6=LC1 | /DFBC003-1/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_516 | =L4=JL1+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L4=JL1 | =L4=JL1 | /BC149
Cable_Id_517 | =L4=JL1+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L4=JL1 | =L4=JL1 | /BC149
Cable_Id_518 | =L4=JL2+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L4=JL2 | =L4=JL2 | /INTERNAL
Cable_Id_519 | =L4=JL2+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L4=JL2 | =L4=JL2 | /INTERNAL
Cable_Id_520 | =L4=JL3+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L4=JL3 | =L4=JL3 | /INTERNAL
Cable_Id_521 | =L4=JL3+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L4=JL3 | =L4=JL3 | /INTERNAL
Cable_Id_522 | =L4=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =L4=LC1 | =L6=LC1 | /DFBC003-2/DFC002/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_523 | =L4=LC1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =L4=LC1 | =L6=LC1 | /DFBC003-2/DFC002/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_524 | =L4=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L4=LC1 | =L6=LC1 | /DFBC003-2/DFC002/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_525 | =L4=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L4=LC1 | =L6=LC1 | /DFBC003-2/DFC002/DFC001/DFC005/DFC006/DFC014/DFC013
Cable_Id_526 | =L5=JL1+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L5=JL1 | =L5=JL1 | /BC011/C116/BC012
Cable_Id_527 | =L5=JL1+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L5=JL1 | =L5=JL1 | /BC011/C116/BC012
Cable_Id_528 | =L5=JL1+1=WHA1 | 4G 62.5/125μm OM1 | =L5=JL1 | =L5=LC1 | /BC011/C010/C009/C008/C105-1/C104/C102/C101/C001/DFC006/DFBC001-2
Cable_Id_529 | =L5=JL2+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L5=JL2 | =L5=JL2 | /INTERNAL
Cable_Id_530 | =L5=JL2+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L5=JL2 | =L5=JL2 | /INTERNAL
Cable_Id_531 | =L5=JL2+1=WHA1 | 4G 62.5/125μm OM1 | =L5=JL2 | =L5=JL1 | /BC011/C010/C009/C008/C105-1/C105-2/C004/BC003/BC004/BC166-1
Cable_Id_532 | =L5=JL3+1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L5=JL3 | =L5=JL3 | /INTERNAL
Cable_Id_533 | =L5=JL3+1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | =L5=JL3 | =L5=JL3 | /INTERNAL
Cable_Id_534 | =L5=JL3+1=WHA1 | 4G 62.5/125μm OM1 | =L5=JL3 | =L5=JL2 | /BC166-1/BC004/BC003/C004/C105-2/C105-1/C104/C102/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/BC019-1
Cable_Id_535 | =L5=JL3+2=WHA1 | 4G 62.5/125μm OM1 | =L5=JL3 | =L5=LC1 | /BC019-1/C138-1/C143-5/C143-4/C143-3/C143-2/C143-1/C002/DFC003/DFC002/DFC001/DFC005/DFBC001-2
Cable_Id_536 | =L5=LC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =L5=LC1 | =L6=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_537 | =L5=LC1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =L5=LC1 | =L6=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_538 | =L5=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | =L5=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_539 | =L5=LC1=WGB2 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | =L5=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_540 | =L5=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | =L5=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_541 | =L5=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L5=LC1 | =L6=LC1 | /DFBC001-2/DFC006/DFC014/DFC013
Cable_Id_542 | =L6=LC1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_543 | =L6=LC1=WGB2 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_544 | =L6=LC1=WGB3 | CAT.6A FRNC FC 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_545 | =L6=LC1=WGB4 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_546 | =L6=LC1=WGB5 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_547 | =L6=LC1=WGB6 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_548 | =L6=LC1=WGB7 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_549 | =L6=LC1=WGB8 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_550 | =L6=LC1=WGB9 | CAT.6A S/FTP 4x2xAWG23 | =L6=LC1 | LOCAL CONTROL ROOM | /BC001/BC002/SECONDARY
Cable_Id_551 | =P1=LC1=WGA5 | RE-2X(St)H PiMF 8x2x0.75mm² | =P1=LC1 | =L5=LC1 | /DFBC001-2/DFC006/BC001/BC002
Cable_Id_552 | =P1=LC1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =P1=LC1 | =L5=LC1 | /DFBC001-2/DFC006/BC001/BC002
Cable_Id_553 | TAG TBA BAS1 | RE-2X(St)H PiMF 4x2x0.75mm² | BAS | =P1=LC1
Cable_Id_554 | TAG TBA BAS2 | RE-2X(St)H PiMF 8x2x0.75mm² | BAS | =P1=LC1
Cable_Id_555 | TAG TBA FDS1 | RE-2X(St)H PiMF 4x2x0.75mm² | FDS | =P1=LC1
Cable_Id_556 | TAG TBA FDS2 | RE-2X(St)H PiMF 8x2x0.75mm² | FDS | =P1=LC1
Cable_Id_557 | TAG TBA HVAC1 | RE-2X(St)H PiMF 8x2x0.75mm² | HVAC | =P1=LC1
Cable_Id_558 | TAG TBA HVAC2 | RE-2X(St)H PiMF 4x2x0.75mm² | HVAC | =P1=LC1
Cable_Id_559 | TAG TBA HVSG1 | RE-2X(St)H PiMF 8x2x0.75mm² | HVSG | =H1=KF1=TAC1 | /SECONDARY/DFC013/DFC007/DFC008/DFC009/DFC010/DFC004-2/DFC004-1/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-2
Cable_Id_560 | TAG TBA PLANT SIS1 | RE-2X(St)H PiMF 4x2x0.75mm² | PLANT SIS | =L1=LC1
Cable_Id_561 | TAG TBA PLANT SIS2 | RE-2X(St)H PiMF 8x2x0.75mm² | PLANT SIS | =L1=LC1
Cable_Id_562 | =H2=JF1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H2=JF1=QMA1 | =L2=JL1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_563 | =H2=JF1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H2=JF1=QMA1 | =L2=JL1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_564 | =H2=JF1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JF1=QMA1 | =L2=JL1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_565 | =H2=JF2=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JF2=BFA1 | =L2=JL1 | /BC121/BC120/SECONDARY
Cable_Id_566 | =H2=JF3=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JF3=BFA1 | =L5=JL3 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_567 | =H2=JF3=BFA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JF3=BFA2 | =L5=JL3 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC031
Cable_Id_568 | =H2=JG1=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JG1=BFA1 | =L2=JL1 | /BC121/BC122/BC124/SECONDARY
Cable_Id_569 | =H2=JG1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H2=JG1=QMA1 | =L2=JL3 | /C125/BC124/BC123/SECONDARY
Cable_Id_570 | =H2=JG1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H2=JG1=QMA1 | =L2=JL3 | /C125/BC124/BC123/SECONDARY
Cable_Id_571 | =H2=JG1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H2=JG1=QMA1 | =L2=JL3 | /C125/BC124/BC123/SECONDARY
Cable_Id_572 | =H2=KC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=KC1=UCA1 | =L2=JL2 | /C127/BC120/SECONDARY
Cable_Id_573 | =H2=KC1=UCA1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=KC1=UCA1 | =L2=JL2 | /C127/BC120/SECONDARY
Cable_Id_574 | =H2=KC1=UCA1=WGA3 | RE-2X(St)H PiMF 4x2x0.75mm² | =H2=KC1=UCA1 | =L2=JL2 | /C127/BC120/SECONDARY
Cable_Id_575 | =H2=KC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=KC1=UCA1 | =L2=JL2 | /C127/BC120/SECONDARY
Cable_Id_576 | =H2=KF1=TAA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=KF1=TAA1 | =H2=KF1=TAC1 | /BC022-1/BC025/C143-3/BC175/BC030
Cable_Id_577 | =H2=KF1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_578 | =H2=KF1=TAC1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_579 | =H2=KF1=TAC1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_580 | =H2=KF1=TAC1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_581 | =H2=KF1=TAC1=WGA5 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_582 | =H2=KF1=TAC1=WGA6 | RE-2X(St)H PiMF 4x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_583 | =H2=KF1=TAC1=WGA7 | RE-2X(St)H PiMF 4x2x0.75mm² | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_584 | =H2=KF1=TAC1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H2=KF1=TAC1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_585 | =H2=LC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H2=LC1=UCA1 | =L2=LC1 | /DFC015
Cable_Id_586 | =H2=LC1=UCA1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H2=LC1=UCA1 | =L2=LC1 | /DFC015
Cable_Id_587 | =H2=LC1=UCA1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=LC1=UCA1 | =L2=LC1 | /DFC015
Cable_Id_588 | =H2=LC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H2=LC1=UCA1 | =L2=LC1 | /DFC015
Cable_Id_589 | =H2=LC1=UCA1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H2=LC1=UCA1 | =L6=LC1 | /DFC013/DFC014/C001/C101/C106/C107-1/C108/C123/C124/C125/C126/C127
Cable_Id_590 | =H2=LC1=UCA1=WGB2 | CAT.6A S/FTP 4x2xAWG23 | =H2=LC1=UCA1 | =L2=LC1 | /DFC015
Cable_Id_591 | =H3=JF1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H3=JF1=QMA1 | =L3=JL1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_592 | =H3=JF1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H3=JF1=QMA1 | =L3=JL1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_593 | =H3=JF1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JF1=QMA1 | =L3=JL1 | /BC135/BC136/BC137/SECONDARY
Cable_Id_594 | =H3=JF2=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JF2=BFA1 | =L3=JL1 | /BC135/BC134/SECONDARY
Cable_Id_595 | =H3=JF3=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JF3=BFA1 | =L5=JL3 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_596 | =H3=JF3=BFA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JF3=BFA2 | =L5=JL3 | /BC019-1/C138-1/C143-5/BC176/BC034/BC021
Cable_Id_597 | =H3=JG1=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JG1=BFA1 | =L3=JL1 | /BC135/BC136/BC138/SECONDARY
Cable_Id_598 | =H3=JG1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H3=JG1=QMA1 | =L3=JL3 | /C130/BC138/BC137/SECONDARY
Cable_Id_599 | =H3=JG1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H3=JG1=QMA1 | =L3=JL3 | /C130/BC138/BC137/SECONDARY
Cable_Id_600 | =H3=JG1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H3=JG1=QMA1 | =L3=JL3 | /C130/BC138/BC137/SECONDARY
Cable_Id_601 | =H3=KC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=KC1=UCA1 | =L3=JL2 | /C132/BC134/SECONDARY
Cable_Id_602 | =H3=KC1=UCA1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=KC1=UCA1 | =L3=JL2 | /C132/BC134/SECONDARY
Cable_Id_603 | =H3=KC1=UCA1=WGA3 | RE-2X(St)H PiMF 4x2x0.75mm² | =H3=KC1=UCA1 | =L3=JL2 | /C132/BC134/SECONDARY
Cable_Id_604 | =H3=KC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=KC1=UCA1 | =L3=JL2 | /C132/BC134/SECONDARY
Cable_Id_605 | =H3=KF1=TAA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=KF1=TAA1 | =H3=KF1=TAC1 | /BC021/BC034/BC176/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_606 | =H3=KF1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_607 | =H3=KF1=TAC1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_608 | =H3=KF1=TAC1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_609 | =H3=KF1=TAC1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_610 | =H3=KF1=TAC1=WGA5 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_611 | =H3=KF1=TAC1=WGA6 | RE-2X(St)H PiMF 4x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_612 | =H3=KF1=TAC1=WGA7 | RE-2X(St)H PiMF 4x2x0.75mm² | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_613 | =H3=KF1=TAC1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H3=KF1=TAC1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_614 | =H3=LC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H3=LC1=UCA1 | =L3=LC1 | /DFC015
Cable_Id_615 | =H3=LC1=UCA1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H3=LC1=UCA1 | =L3=LC1 | /DFC015
Cable_Id_616 | =H3=LC1=UCA1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=LC1=UCA1 | =L3=LC1 | /DFC015
Cable_Id_617 | =H3=LC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H3=LC1=UCA1 | =L3=LC1 | /DFC015
Cable_Id_618 | =H3=LC1=UCA1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H3=LC1=UCA1 | =L6=LC1 | /DFC013/DFC014/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/C130/C131/C132
Cable_Id_619 | =H3=LC1=UCA1=WGB2 | CAT.6A S/FTP 4x2xAWG23 | =H3=LC1=UCA1 | =L3=LC1 | /DFC015
Cable_Id_620 | =H4=JF1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H4=JF1=QMA1 | =L4=JL1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_621 | =H4=JF1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H4=JF1=QMA1 | =L4=JL1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_622 | =H4=JF1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JF1=QMA1 | =L4=JL1 | /BC149/BC150/BC151/SECONDARY
Cable_Id_623 | =H4=JF2=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JF2=BFA1 | =L4=JL1 | /BC149/BC148/SECONDARY
Cable_Id_624 | =H4=JF3=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JF3=BFA1 | =L5=JL3 | /BC019-1/C138-1/BC180/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_625 | =H4=JF3=BFA2=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JF3=BFA2 | =L5=JL3 | /BC019-1/C138-1/C143-5/BC176/BC034/BC035
Cable_Id_626 | =H4=JG1=BFA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JG1=BFA1 | =L4=JL1 | /BC149/BC150/BC152/SECONDARY
Cable_Id_627 | =H4=JG1=QMA1=WDB1 | RE-2X(St)H 1x2x0.75mm² | =H4=JG1=QMA1 | =L4=JL3 | /C135/BC152/BC151/SECONDARY
Cable_Id_628 | =H4=JG1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H4=JG1=QMA1 | =L4=JL3 | /C135/BC152/BC151/SECONDARY
Cable_Id_629 | =H4=JG1=QMA1=WGB1 | CAT.6A FRNC FC 4x2xAWG23 | =H4=JG1=QMA1 | =L4=JL3 | /C135/BC152/BC151/SECONDARY
Cable_Id_630 | =H4=KC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=KC1=UCA1 | =L4=JL2 | /C137/BC148/SECONDARY
Cable_Id_631 | =H4=KC1=UCA1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=KC1=UCA1 | =L4=JL2 | /C137/BC148/SECONDARY
Cable_Id_632 | =H4=KC1=UCA1=WGA3 | RE-2X(St)H PiMF 4x2x0.75mm² | =H4=KC1=UCA1 | =L4=JL2 | /C137/BC148/SECONDARY
Cable_Id_633 | =H4=KC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=KC1=UCA1 | =L4=JL2 | /C137/BC148/SECONDARY
Cable_Id_634 | =H4=KF1=TAA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=KF1=TAA1 | =H4=KF1=TAC1 | /BC023-1/BC026/C107-6/C107-5/BC176/BC034
Cable_Id_635 | =H4=KF1=TAC1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_636 | =H4=KF1=TAC1=WGA2 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_637 | =H4=KF1=TAC1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_638 | =H4=KF1=TAC1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_639 | =H4=KF1=TAC1=WGA5 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_640 | =H4=KF1=TAC1=WGA6 | RE-2X(St)H PiMF 4x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_641 | =H4=KF1=TAC1=WGA7 | RE-2X(St)H PiMF 4x2x0.75mm² | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_642 | =H4=KF1=TAC1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H4=KF1=TAC1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_643 | =H4=LC1=UCA1=WGA1 | RE-2X(St)H PiMF 8x2x0.75mm² | =H4=LC1=UCA1 | =L4=LC1 | /DFC015
Cable_Id_644 | =H4=LC1=UCA1=WGA2 | RE-2X(St)H PiMF 4x2x0.75mm² | =H4=LC1=UCA1 | =L4=LC1 | /DFC015
Cable_Id_645 | =H4=LC1=UCA1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=LC1=UCA1 | =L4=LC1 | /DFC015
Cable_Id_646 | =H4=LC1=UCA1=WGA4 | RE-2X(St)H PiMF 2x2x0.75mm² | =H4=LC1=UCA1 | =L4=LC1 | /DFC015
Cable_Id_647 | =H4=LC1=UCA1=WGB1 | CAT.6A S/FTP 4x2xAWG23 | =H4=LC1=UCA1 | =L6=LC1 | /DFC013/DFC014/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/C135/C136/C137
Cable_Id_648 | =H4=LC1=UCA1=WGB2 | CAT.6A S/FTP 4x2xAWG23 | =H4=LC1=UCA1 | =L4=LC1 | /DFC015
Cable_Id_649 | TAG TBA HVSG2 | RE-2X(St)H PiMF 8x2x0.75mm² | HVSG | =H2=KF1=TAC1 | /SECONDARY/DFC013/DFC007/DFC008/DFC009/DFC010/DFC004-2/DFC004-1/DFC003/C002/C143-1/C143-2/C143-3/BC025/BC022-1
Cable_Id_650 | TAG TBA HVSG3 | RE-2X(St)H PiMF 8x2x0.75mm² | HVSG | =H3=KF1=TAC1 | /SECONDARY/DFC013/DFC007/DFC008/DFC009/DFC010/DFC004-2/DFC004-1/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1/BC023-2
Cable_Id_651 | TAG TBA HVSG4 | RE-2X(St)H PiMF 8x2x0.75mm² | HVSG | =H4=KF1=TAC1 | /SECONDARY/DFC013/DFC007/DFC008/DFC009/DFC010/DFC004-2/DFC004-1/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/BC026/BC023-1
Cable_Id_652 | =L2=JL1+1=WHA1 | 4G 62.5/125μm OM1 | =L2=JL1 | =L2=LC1 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C107-1/C108/C123/C124/BC124/BC122/BC121
Cable_Id_653 | =L2=JL2+1=WHA1 | 4G 62.5/125μm OM1 | =L2=JL2 | =L2=JL1 | /BC121/BC120/C127
Cable_Id_654 | =L2=JL3+1=WHA1 | 4G 62.5/125μm OM1 | =L2=JL2 | =L2=JL3 | /C127/C126/C125
Cable_Id_655 | =L2=LC1=WHA1 | 4G 62.5/125μm OM1 | =L2=LC1 | =L2=JL3 | /DFBC002-2/DFC001/DFC002/DFC003/C002/C107-1/C108/C123/C124/C125
Cable_Id_656 | TAG TBA PLANT SIS3 | RE-2X(St)H PiMF 4x2x0.75mm² | PLANT SIS | =L2=LC1
Cable_Id_657 | TAG TBA PLANT SIS4 | RE-2X(St)H PiMF 8x2x0.75mm² | PLANT SIS | =L2=LC1
Cable_Id_658 | =L3=JL1+1=WHA1 | 4G 62.5/125μm OM1 | =L3=JL1 | =L3=LC1 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/BC138/BC136/BC135
Cable_Id_659 | =L3=JL2+1=WHA1 | 4G 62.5/125μm OM1 | =L3=JL2 | =L3=JL1 | /BC135/BC134/C132
Cable_Id_660 | =L3=JL3+1=WHA1 | 4G 62.5/125μm OM1 | =L3=JL2 | =L3=JL3 | /C132/C131/C130
Cable_Id_661 | =L3=LC1=WHA1 | 4G 62.5/125μm OM1 | =L3=LC1 | =L3=JL3 | /DFBC003-1/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/C130
Cable_Id_662 | TAG TBA PLANT SIS5 | RE-2X(St)H PiMF 4x2x0.75mm² | PLANT SIS | =L3=LC1
Cable_Id_663 | TAG TBA PLANT SIS6 | RE-2X(St)H PiMF 8x2x0.75mm² | PLANT SIS | =L3=LC1
Cable_Id_664 | =L4=JL1+1=WHA1 | 4G 62.5/125μm OM1 | =L4=JL1 | =L4=LC1 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/BC152/BC150/BC149
Cable_Id_665 | =L4=JL2+1=WHA1 | 4G 62.5/125μm OM1 | =L4=JL2 | =L4=JL1 | /BC149/BC148/C137
Cable_Id_666 | =L4=JL3+1=WHA1 | 4G 62.5/125μm OM1 | =L4=JL2 | =L4=JL3 | /C137/C136/C135
Cable_Id_667 | =L4=LC1=WHA1 | 4G 62.5/125μm OM1 | =L4=LC1 | =L4=JL3 | /DFBC003-2/DFC002/DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/C133/C134/C135
Cable_Id_668 | TAG TBA PLANT SIS7 | RE-2X(St)H PiMF 4x2x0.75mm² | PLANT SIS | =L4=LC1
Cable_Id_669 | TAG TBA PLANT SIS8 | RE-2X(St)H PiMF 8x2x0.75mm² | PLANT SIS | =L4=LC1
Cable_Id_670 | =H1=KF1=TAC1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_671 | =H1=KF1=TAC1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_672 | =H1=KF1=TAC1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_673 | =H1=KF1=TAC1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_674 | =H1=KF1=TAC1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_675 | =H1=KF1=TAC1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_676 | =H1=KF1=TAC1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_677 | =H1=KF1=TAC1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_678 | =H1=KF1=TAC1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_679 | =H1=KF1=TAC1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_680 | =H1=KF1=TAC1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_681 | =H1=KF1=TAC1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A003
Cable_Id_682 | =H1=KF1=TAC1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_683 | =H1=KF1=TAC1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_684 | =H1=KF1=TAC1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_685 | =H1=KF1=TAC1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_686 | =H1=KF1=TAC1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_687 | =H1=KF1=TAC1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_688 | =H1=KF1=TAC1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_689 | =H1=KF1=TAC1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_690 | =H1=KF1=TAC1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_691 | =H1=KF1=TAC1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_692 | =H1=KF1=TAC1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_693 | =H1=KF1=TAC1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.1 | =H1=KF1=TAC1-X1.1 | /SECONDARY/A004
Cable_Id_694 | =H1=KF1=TAC1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H1=KF1=TAA1-X1.1.1 | =H1=KF1=TAC1-X1.1.1 | /SECONDARY/A004
Cable_Id_695 | =H1=KF1=TAC1=WBB25 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_696 | =H1=KF1=TAC1=WBB26 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_697 | =H1=KF1=TAC1=WBB27 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_698 | =H1=KF1=TAC1=WBB28 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_699 | =H1=KF1=TAC1=WBB29 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_700 | =H1=KF1=TAC1=WBB30 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_701 | =H1=KF1=TAC1=WBB31 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_702 | =H1=KF1=TAC1=WBB32 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_703 | =H1=KF1=TAC1=WBB33 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_704 | =H1=KF1=TAC1=WBB34 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_705 | =H1=KF1=TAC1=WBB35 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_706 | =H1=KF1=TAC1=WBB36 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A007
Cable_Id_707 | =H1=KF1=TAC1=WBB37 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_708 | =H1=KF1=TAC1=WBB38 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_709 | =H1=KF1=TAC1=WBB39 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_710 | =H1=KF1=TAC1=WBB40 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_711 | =H1=KF1=TAC1=WBB41 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_712 | =H1=KF1=TAC1=WBB42 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_713 | =H1=KF1=TAC1=WBB43 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_714 | =H1=KF1=TAC1=WBB44 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_715 | =H1=KF1=TAC1=WBB45 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_716 | =H1=KF1=TAC1=WBB46 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_717 | =H1=KF1=TAC1=WBB47 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_718 | =H1=KF1=TAC1=WBB48 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H1=KF1=TAA1-X1.2 | =H1=KF1=TAC1-X1.2 | /SECONDARY/A008
Cable_Id_719 | =H1=KF1=MAA1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H1=KF1=TAC1-PE | =H1=KF1=MAA1-PE | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_720 | =H1=KF1=MAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_721 | =H1=KF1=MAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_722 | =H1=KF1=MAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_723 | =H1=KF1=MAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_724 | =H1=KF1=MAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_725 | =H1=KF1=MAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_726 | =H1=KF1=MAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_727 | =H1=KF1=MAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-U01 | =H1=KF1=MAA1-U1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_728 | =H1=KF1=MAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_729 | =H1=KF1=MAA1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_730 | =H1=KF1=MAA1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_731 | =H1=KF1=MAA1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A039/A101/A127/A105/UNDERGROUND_PIPE/A108
Cable_Id_732 | =H1=KF1=MAA1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_733 | =H1=KF1=MAA1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_734 | =H1=KF1=MAA1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_735 | =H1=KF1=MAA1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-V01 | =H1=KF1=MAA1-V1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_736 | =H1=KF1=MAA1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_737 | =H1=KF1=MAA1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_738 | =H1=KF1=MAA1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_739 | =H1=KF1=MAA1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_740 | =H1=KF1=MAA1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_741 | =H1=KF1=MAA1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_742 | =H1=KF1=MAA1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_743 | =H1=KF1=MAA1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H1=KF1=TAC1-W01 | =H1=KF1=MAA1-W1 | /A034/A103/A128/A106/UNDERGROUND_PIPE/A107
Cable_Id_744 | =H2=KF1=TAC1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_745 | =H2=KF1=TAC1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_746 | =H2=KF1=TAC1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_747 | =H2=KF1=TAC1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_748 | =H2=KF1=TAC1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_749 | =H2=KF1=TAC1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_750 | =H2=KF1=TAC1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_751 | =H2=KF1=TAC1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_752 | =H2=KF1=TAC1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_753 | =H2=KF1=TAC1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_754 | =H2=KF1=TAC1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_755 | =H2=KF1=TAC1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A011
Cable_Id_756 | =H2=KF1=TAC1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_757 | =H2=KF1=TAC1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_758 | =H2=KF1=TAC1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_759 | =H2=KF1=TAC1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_760 | =H2=KF1=TAC1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_761 | =H2=KF1=TAC1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_762 | =H2=KF1=TAC1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_763 | =H2=KF1=TAC1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_764 | =H2=KF1=TAC1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_765 | =H2=KF1=TAC1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_766 | =H2=KF1=TAC1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_767 | =H2=KF1=TAC1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.1 | =H2=KF1=TAC1-X1.1 | /SECONDARY/A012
Cable_Id_768 | =H2=KF1=TAC1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H2=KF1=TAA1-X1.1.1 | =H2=KF1=TAC1-X1.1.1 | /SECONDARY/A012
Cable_Id_769 | =H2=KF1=TAC1=WBB25 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_770 | =H2=KF1=TAC1=WBB26 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_771 | =H2=KF1=TAC1=WBB27 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_772 | =H2=KF1=TAC1=WBB28 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_773 | =H2=KF1=TAC1=WBB29 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_774 | =H2=KF1=TAC1=WBB30 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_775 | =H2=KF1=TAC1=WBB31 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_776 | =H2=KF1=TAC1=WBB32 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_777 | =H2=KF1=TAC1=WBB33 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_778 | =H2=KF1=TAC1=WBB34 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_779 | =H2=KF1=TAC1=WBB35 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_780 | =H2=KF1=TAC1=WBB36 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A015
Cable_Id_781 | =H2=KF1=TAC1=WBB37 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_782 | =H2=KF1=TAC1=WBB38 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_783 | =H2=KF1=TAC1=WBB39 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_784 | =H2=KF1=TAC1=WBB40 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_785 | =H2=KF1=TAC1=WBB41 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_786 | =H2=KF1=TAC1=WBB42 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_787 | =H2=KF1=TAC1=WBB43 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_788 | =H2=KF1=TAC1=WBB44 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_789 | =H2=KF1=TAC1=WBB45 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_790 | =H2=KF1=TAC1=WBB46 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_791 | =H2=KF1=TAC1=WBB47 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_792 | =H2=KF1=TAC1=WBB48 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H2=KF1=TAA1-X1.2 | =H2=KF1=TAC1-X1.2 | /SECONDARY/A016
Cable_Id_793 | =H2=KF1=MAA1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H2=KF1=TAC1-PE | =H2=KF1=MAA1-PE | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_794 | =H2=KF1=MAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_795 | =H2=KF1=MAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_796 | =H2=KF1=MAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_797 | =H2=KF1=MAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_798 | =H2=KF1=MAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_799 | =H2=KF1=MAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_800 | =H2=KF1=MAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_801 | =H2=KF1=MAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-U01 | =H2=KF1=MAA1-U1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_802 | =H2=KF1=MAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_803 | =H2=KF1=MAA1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_804 | =H2=KF1=MAA1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_805 | =H2=KF1=MAA1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A033/A104/A111//UNDERGROUND_PIPE/A114
Cable_Id_806 | =H2=KF1=MAA1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_807 | =H2=KF1=MAA1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_808 | =H2=KF1=MAA1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_809 | =H2=KF1=MAA1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-V01 | =H2=KF1=MAA1-V1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_810 | =H2=KF1=MAA1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_811 | =H2=KF1=MAA1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_812 | =H2=KF1=MAA1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_813 | =H2=KF1=MAA1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_814 | =H2=KF1=MAA1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_815 | =H2=KF1=MAA1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_816 | =H2=KF1=MAA1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_817 | =H2=KF1=MAA1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H2=KF1=TAC1-W01 | =H2=KF1=MAA1-W1 | /A040/A102/A112/UNDERGROUND_PIPE/A113
Cable_Id_818 | =H3=KF1=TAC1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_819 | =H3=KF1=TAC1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_820 | =H3=KF1=TAC1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_821 | =H3=KF1=TAC1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_822 | =H3=KF1=TAC1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_823 | =H3=KF1=TAC1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_824 | =H3=KF1=TAC1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_825 | =H3=KF1=TAC1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_826 | =H3=KF1=TAC1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_827 | =H3=KF1=TAC1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_828 | =H3=KF1=TAC1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_829 | =H3=KF1=TAC1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A023
Cable_Id_830 | =H3=KF1=TAC1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_831 | =H3=KF1=TAC1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_832 | =H3=KF1=TAC1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_833 | =H3=KF1=TAC1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_834 | =H3=KF1=TAC1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_835 | =H3=KF1=TAC1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_836 | =H3=KF1=TAC1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_837 | =H3=KF1=TAC1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_838 | =H3=KF1=TAC1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_839 | =H3=KF1=TAC1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_840 | =H3=KF1=TAC1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_841 | =H3=KF1=TAC1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.1 | =H3=KF1=TAC1-X1.1 | /SECONDARY/A024
Cable_Id_842 | =H3=KF1=TAC1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H3=KF1=TAA1-X1.1.1 | =H3=KF1=TAC1-X1.1.1 | /SECONDARY/A024
Cable_Id_843 | =H3=KF1=TAC1=WBB25 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_844 | =H3=KF1=TAC1=WBB26 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_845 | =H3=KF1=TAC1=WBB27 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_846 | =H3=KF1=TAC1=WBB28 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_847 | =H3=KF1=TAC1=WBB29 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_848 | =H3=KF1=TAC1=WBB30 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_849 | =H3=KF1=TAC1=WBB31 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_850 | =H3=KF1=TAC1=WBB32 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_851 | =H3=KF1=TAC1=WBB33 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_852 | =H3=KF1=TAC1=WBB34 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_853 | =H3=KF1=TAC1=WBB35 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_854 | =H3=KF1=TAC1=WBB36 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A019
Cable_Id_855 | =H3=KF1=TAC1=WBB37 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_856 | =H3=KF1=TAC1=WBB38 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_857 | =H3=KF1=TAC1=WBB39 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_858 | =H3=KF1=TAC1=WBB40 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_859 | =H3=KF1=TAC1=WBB41 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_860 | =H3=KF1=TAC1=WBB42 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_861 | =H3=KF1=TAC1=WBB43 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_862 | =H3=KF1=TAC1=WBB44 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_863 | =H3=KF1=TAC1=WBB45 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_864 | =H3=KF1=TAC1=WBB46 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_865 | =H3=KF1=TAC1=WBB47 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_866 | =H3=KF1=TAC1=WBB48 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H3=KF1=TAA1-X1.2 | =H3=KF1=TAC1-X1.2 | /SECONDARY/A020
Cable_Id_867 | =H3=KF1=MAA1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H3=KF1=TAC1-PE | =H3=KF1=MAA1-PE | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_868 | =H3=KF1=MAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_869 | =H3=KF1=MAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_870 | =H3=KF1=MAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_871 | =H3=KF1=MAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_872 | =H3=KF1=MAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_873 | =H3=KF1=MAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_874 | =H3=KF1=MAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_875 | =H3=KF1=MAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-U01 | =H3=KF1=MAA1-U1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_876 | =H3=KF1=MAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_877 | =H3=KF1=MAA1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_878 | =H3=KF1=MAA1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_879 | =H3=KF1=MAA1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A037/A115/A119/UNDERGROUND_PIPE/A122
Cable_Id_880 | =H3=KF1=MAA1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_881 | =H3=KF1=MAA1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_882 | =H3=KF1=MAA1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_883 | =H3=KF1=MAA1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-V01 | =H3=KF1=MAA1-V1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_884 | =H3=KF1=MAA1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_885 | =H3=KF1=MAA1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_886 | =H3=KF1=MAA1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_887 | =H3=KF1=MAA1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_888 | =H3=KF1=MAA1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_889 | =H3=KF1=MAA1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_890 | =H3=KF1=MAA1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_891 | =H3=KF1=MAA1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H3=KF1=TAC1-W01 | =H3=KF1=MAA1-W1 | /A036/A117/A120/UNDERGROUND_PIPE/A121
Cable_Id_892 | =H4=KF1=TAC1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_893 | =H4=KF1=TAC1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_894 | =H4=KF1=TAC1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_895 | =H4=KF1=TAC1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_896 | =H4=KF1=TAC1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_897 | =H4=KF1=TAC1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_898 | =H4=KF1=TAC1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_899 | =H4=KF1=TAC1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_900 | =H4=KF1=TAC1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_901 | =H4=KF1=TAC1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_902 | =H4=KF1=TAC1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_903 | =H4=KF1=TAC1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A027
Cable_Id_904 | =H4=KF1=TAC1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_905 | =H4=KF1=TAC1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_906 | =H4=KF1=TAC1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_907 | =H4=KF1=TAC1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_908 | =H4=KF1=TAC1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_909 | =H4=KF1=TAC1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_910 | =H4=KF1=TAC1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_911 | =H4=KF1=TAC1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_912 | =H4=KF1=TAC1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_913 | =H4=KF1=TAC1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_914 | =H4=KF1=TAC1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_915 | =H4=KF1=TAC1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.1 | =H4=KF1=TAC1-X1.1 | /SECONDARY/A028
Cable_Id_916 | =H4=KF1=TAC1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H4=KF1=TAA1-X1.1.1 | =H4=KF1=TAC1-X1.1.1 | /SECONDARY/A028
Cable_Id_917 | =H4=KF1=TAC1=WBB25 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_918 | =H4=KF1=TAC1=WBB26 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_919 | =H4=KF1=TAC1=WBB27 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_920 | =H4=KF1=TAC1=WBB28 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_921 | =H4=KF1=TAC1=WBB29 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_922 | =H4=KF1=TAC1=WBB30 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_923 | =H4=KF1=TAC1=WBB31 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_924 | =H4=KF1=TAC1=WBB32 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_925 | =H4=KF1=TAC1=WBB33 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_926 | =H4=KF1=TAC1=WBB34 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_927 | =H4=KF1=TAC1=WBB35 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_928 | =H4=KF1=TAC1=WBB36 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A031
Cable_Id_929 | =H4=KF1=TAC1=WBB37 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_930 | =H4=KF1=TAC1=WBB38 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_931 | =H4=KF1=TAC1=WBB39 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_932 | =H4=KF1=TAC1=WBB40 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_933 | =H4=KF1=TAC1=WBB41 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_934 | =H4=KF1=TAC1=WBB42 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_935 | =H4=KF1=TAC1=WBB43 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_936 | =H4=KF1=TAC1=WBB44 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_937 | =H4=KF1=TAC1=WBB45 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_938 | =H4=KF1=TAC1=WBB46 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_939 | =H4=KF1=TAC1=WBB47 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_940 | =H4=KF1=TAC1=WBB48 | N2XS(FL)H 12/20kV (24)kV 1x300/25mm² | =H4=KF1=TAA1-X1.2 | =H4=KF1=TAC1-X1.2 | /SECONDARY/A032
Cable_Id_941 | =H4=KF1=MAA1=WEB1 | RZ1-K GREEN/YELLOW 0.6/1 kV 1x185mm² | =H4=KF1=TAC1-PE | =H4=KF1=MAA1-PE | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_942 | =H4=KF1=MAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_943 | =H4=KF1=MAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_944 | =H4=KF1=MAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_945 | =H4=KF1=MAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_946 | =H4=KF1=MAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_947 | =H4=KF1=MAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_948 | =H4=KF1=MAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_949 | =H4=KF1=MAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-U01 | =H4=KF1=MAA1-U1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_950 | =H4=KF1=MAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_951 | =H4=KF1=MAA1=WBB10 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_952 | =H4=KF1=MAA1=WBB11 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_953 | =H4=KF1=MAA1=WBB12 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A035/A118/A130/A123/UNDERGROUND_PIPE/A126
Cable_Id_954 | =H4=KF1=MAA1=WBB13 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_955 | =H4=KF1=MAA1=WBB14 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_956 | =H4=KF1=MAA1=WBB15 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_957 | =H4=KF1=MAA1=WBB16 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-V01 | =H4=KF1=MAA1-V1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_958 | =H4=KF1=MAA1=WBB17 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_959 | =H4=KF1=MAA1=WBB18 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_960 | =H4=KF1=MAA1=WBB19 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_961 | =H4=KF1=MAA1=WBB20 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_962 | =H4=KF1=MAA1=WBB21 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_963 | =H4=KF1=MAA1=WBB22 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_964 | =H4=KF1=MAA1=WBB23 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_965 | =H4=KF1=MAA1=WBB24 | N2XS(FL)H 12/20kV (24)kV 1x185/25mm² | =H4=KF1=TAC1-W01 | =H4=KF1=MAA1-W1 | /A038/A116/A129/A124/UNDERGROUND_PIPE/A125
Cable_Id_966 | =H1=KF1=TAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_967 | =H1=KF1=TAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_968 | =H1=KF1=TAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_969 | =H1=KF1=TAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_970 | =H1=KF1=TAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_971 | =H1=KF1=TAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_972 | =H1=KF1=TAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_973 | =H1=KF1=TAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_974 | =H1=KF1=TAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X1 | =H1=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_975 | =H2=KF1=TAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_976 | =H2=KF1=TAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_977 | =H2=KF1=TAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_978 | =H2=KF1=TAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_979 | =H2=KF1=TAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_980 | =H2=KF1=TAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_981 | =H2=KF1=TAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_982 | =H2=KF1=TAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_983 | =H2=KF1=TAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X2 | =H2=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_984 | =H3=KF1=TAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_985 | =H3=KF1=TAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_986 | =H3=KF1=TAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_987 | =H3=KF1=TAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_988 | =H3=KF1=TAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_989 | =H3=KF1=TAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_990 | =H3=KF1=TAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_991 | =H3=KF1=TAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_992 | =H3=KF1=TAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X3 | =H3=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_993 | =H4=KF1=TAA1=WBB1 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_994 | =H4=KF1=TAA1=WBB2 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_995 | =H4=KF1=TAA1=WBB3 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_996 | =H4=KF1=TAA1=WBB4 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_997 | =H4=KF1=TAA1=WBB5 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_998 | =H4=KF1=TAA1=WBB6 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_999 | =H4=KF1=TAA1=WBB7 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_1000 | =H4=KF1=TAA1=WBB8 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_1001 | =H4=KF1=TAA1=WBB9 | N2XS(FL)H 12/20kV (24)kV 1x240/25mm² | HVSG-X4 | =H4=KF1=TAA1-X5 | /UNDERGROUND_PIPE
Cable_Id_1002 | =F2=EBB1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G10mm² | =F2=EBB1=UCA1-X1 | =K1=JK2+13+13G1-13G1.XD1 | /DFB012/DFB011/DFB010/DFB009/DFB008/DFB007/DFB006/DFB005/DFB004/DFB003/DFB002/DFB001/DFB014/DFB015/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/B116/BC168/SECONDARY
Cable_Id_1003 | =F2=KF1=GQA1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=MAA1 | =F2=KF1=GQA1=XDC2-X3 | /SECONDARY
Cable_Id_1004 | =F2=KF1=GQA1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G25mm² | =F2=KF1=GQA1=XDC1-X1 | =F2=KF1=GQA1=MAA1 | /SECONDARY
Cable_Id_1005 | =F2=KF1=GQA1=XDC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2-X3 | =K1=JK2+12-=F2=KF1=GQA1=TAC1 | /DFC011/DFC004-1/DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C104/C105-1/C105-2/C004/C005/C011/C141/C142/SECONDARY
Cable_Id_1006 | =F2=KF2=GQA1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=MAA1 | =F2=KF2=GQA1=XDC2-X3 | /SECONDARY
Cable_Id_1007 | =F2=KF3=GPB1=MAA1=WAG1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=MAA1 | =F2=KF3=GPB1=XDC2-X3 | /SECONDARY
Cable_Id_1008 | =F2=KF4=GPB1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=MAA1 | =F2=KF4=GPB1=XDC2-X3 | /SECONDARY
Cable_Id_1009 | =F2=KF2=GQA1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G25mm² | =F2=KF2=GQA1=XDC1-X1 | =F2=KF2=GQA1=MAA1 | /SECONDARY
Cable_Id_1010 | =F2=KF2=GQA1=XDC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2-X3 | =K1=JK2+12-=F2=KF2=GQA1=TAC1 | /DFC011/DFC004-1/DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C104/C105-1/C105-2/C004/C005/C011/C141/C142/SECONDARY
Cable_Id_1011 | =H3=LC1=XDC2=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H3=LC1=XDC2-XG | /SECONDARY
Cable_Id_1012 | =F2=KF3=GPB1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =F2=KF3=GPB1=XDC1-X1 | =F2=KF3=GPB1=MAA1 | /SECONDARY
Cable_Id_1013 | =F2=KF3=GPB1=XDC1=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =F2=KF3=GPB1=XDC1-X1 | =F2=KF3=GPB1=XDC3-S1 | /SECONDARY
Cable_Id_1014 | =F2=KF3=GPB1=XDC2=WAG1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF3=GPB1=XDC2-X3 | =K1=JK2+12-=F2=KF3=GPB1=TAC1 | /DFC011/DFC004-1/DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C104/C105-1/C105-2/C004/C005/C011/C141/BC169
Cable_Id_1015 | =F2=KF4=GPB1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =F2=KF4=GPB1=XDC1-X1 | =F2=KF4=GPB1=MAA1 | /SECONDARY
Cable_Id_1016 | =F2=KF4=GPB1=XDC1=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =F2=KF4=GPB1=XDC1-X1 | =F2=KF4=GPB1=XDC3-S1 | /SECONDARY
Cable_Id_1017 | =F2=KF4=GPB1=XDC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF4=GPB1=XDC2-X3 | =K1=JK2+12-=F2=KF4=GPB1=TAC1 | /DFC011/DFC004-1/DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C104/C105-1/C105-2/C004/C005/C011/C141/C142/BC170
Cable_Id_1018 | =F2=QC1=QMA11=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC1=QMA11=XDC1-S1 | =K1=JK2+8+8Q1-8Q1.XD1 | /DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/BC003/BC177/SECONDARY
Cable_Id_1019 | =F2=QC1=QMA11=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC1=QMA11=XDC1-S1 | VLVZ-XK | /SECONDARY
Cable_Id_1020 | =F2=QC2=QMA11=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC2=QMA11=XDC1-S1 | =K1=JK2+8+8P1-8P1.XD1 | /DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/BC003/BC177/BC178/SECONDARY
Cable_Id_1021 | =F2=QC2=QMA11=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC2=QMA11=XDC1-S1 | VLVZ-XK | /SECONDARY
Cable_Id_1022 | =F2=QC3=QMA11=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC3=QMA11=XDC1-S1 | =K1=JK2+8+8O1-8O1.XD1 | /DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/BC003/BC177/BC178/BC179/SECONDARY
Cable_Id_1023 | =F2=QC3=QMA11=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =F2=QC3=QMA11=XDC1-S1 | VLVZ-XK | /SECONDARY
Cable_Id_1024 | =H1=JF1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H1=JF1=QMA1=XDC1-S1 | =H1=JF1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1025 | =H1=JF1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H1=JF1=QMA1=XDC1-S1 | =K1=JK2+9+9O1-9O1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-1/B118/BC110/BC109/SECONDARY
Cable_Id_1026 | =H1=JG1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H1=JG1=QMA1=XCD1-S1 | =H1=JG1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1027 | =H1=JG1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H1=JG1=QMA1=XCD1-S1 | =K1=JK2+9+9K1-9I1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-1/B118/BC110/BC109/SECONDARY
Cable_Id_1028 | =H1=KC1=HQB1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H1=KC1=UCA1-X1 | =H1=KC1=HQB1=MAA1 | /SECONDARY
Cable_Id_1029 | =H1=KC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G16mm² | =H1=KC1=UCA1-X1 | =K1=JK2+10+10M1-10M1.XD1 | /DFB010/DFB009/DFB008/DFB007/DFB006/DFB005/DFB004/DFB003/DFB002/DFB001/DFB014/DFB015/B001/B101/B102/B104-1/B118/B119/BC106/SECONDARY
Cable_Id_1030 | =H1=KF1=TAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G50mm² | =H1=KF1=TAA1=XDC1-1XT02 | =K1=JK2+3+3M1-3M1.XD1 | /DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/BC175/BC030/BC020/SECONDARY
Cable_Id_1031 | =H1=LC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G6mm² | =H1=LC1=UCA1-40X1 | =K1=JK2+2+2M1-2M1.XD1 | /DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB018-1
Cable_Id_1032 | =H2=JF1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H2=JF1=QMA1=XDC1-S1 | =H2=JF1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1033 | =H2=JF1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H2=JF1=QMA1=XDC1-S1 | =K1=JK2+9+9N1-9N1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B108/B120/BC124/BC123/SECONDARY
Cable_Id_1034 | =H2=JG1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H2=JG1=QMA1=XCD1-S1 | =H2=JG1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1035 | =H2=JG1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H2=JG1=QMA1=XCD1-S1 | =K1=JK2+9+9J1-9J1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B108/B120/BC124/BC123/SECONDARY
Cable_Id_1036 | =H2=KC1=HQB1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H2=KC1=UCA1-X1 | =H2=KC1=HQB1=MAA1 | /SECONDARY
Cable_Id_1037 | =H2=KC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G16mm² | =H2=KC1=UCA1-X1 | =K1=JK2+10+10J1-10J1.XD1 | /DFB010/DFB011/DFB012/DFB013/B002/B107-1/B108/B120/B121/BC120/SECONDARY
Cable_Id_1038 | =H2=KF1=TAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G50mm² | =H2=KF1=TAA1=XDC1-1XT02 | =K1=JK2+3+3J1-3J1.XD1 | /DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/BC175/BC031/SECONDARY
Cable_Id_1039 | =H2=LC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G6mm² | =H2=LC1=UCA1-40X1 | =K1=JK2+2+2J1-2J1.XD1 | /DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB018-1
Cable_Id_1040 | =H3=JF1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H3=JF1=QMA1=XDC1-S1 | =H3=JF1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1041 | =H3=JF1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H3=JF1=QMA1=XDC1-S1 | =K1=JK2+9+9M1-9M1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/BC138/BC137/SECONDARY
Cable_Id_1042 | =H3=JG1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H3=JG1=QMA1=XCD1-S1 | =H3=JG1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1043 | =H3=JG1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H3=JG1=QMA1=XCD1-S1 | =K1=JK2+9+9I1-9I1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/BC138/BC137/SECONDARY
Cable_Id_1044 | =H3=KC1=HQB1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H3=KC1=UCA1-X1 | =H3=KC1=HQB1=MAA1 | /SECONDARY
Cable_Id_1045 | =H3=KF1=TAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G50mm² | =H3=KF1=TAA1=XDC1-1XT02 | =K1=JK2+3+3G1-3G1.XD1 | /DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/BC176/BC034/BC021/SECONDARY
Cable_Id_1046 | =H3=LC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G6mm² | =H3=LC1=UCA1-40X1 | =K1=JK2+2+2G1-2G1.XD1 | /DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB018-2
Cable_Id_1047 | =H4=JF1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H4=JF1=QMA1=XDC1-S1 | =H4=JF1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1048 | =H4=JF1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H4=JF1=QMA1=XDC1-S1 | =K1=JK2+9+9L1-9L1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/BC152/BC151/SECONDARY/SECONDARY
Cable_Id_1049 | =H4=JG1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H4=JG1=QMA1=XCD1-S1 | =H4=JG1=QMA1=MAA1-XK | /SECONDARY
Cable_Id_1050 | =H4=JG1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H4=JG1=QMA1=XCD1-S1 | =K1=JK2+9+9H1-9H1.XD1 | /DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/BC152/BC151/SECONDARY/SECONDARY
Cable_Id_1051 | =H4=KC1=HQB1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H4=KC1=UCA1-X1 | =H4=KC1=HQB1=MAA1 | /SECONDARY
Cable_Id_1052 | =H4=KC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G16mm² | =H4=KC1=UCA1-X1 | =K1=JK2+10+10D1-10D1.XD1 | /DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/B125/BC148/SECONDARY
Cable_Id_1053 | =H4=KF1=TAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G50mm² | =H4=KF1=TAA1=XDC1-1XT02 | =K1=JK2+3+3D1-3D1.XD1 | /DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/BC176/BC035/SECONDARY
Cable_Id_1054 | =H4=LC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G6mm² | =H4=LC1=UCA1-40X1 | =K1=JK2+2+2D1-2D1.XD1 | /DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB018-2
Cable_Id_1055 | =H9=JG1=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QMA1=XDC1-S1 | =H9=JG1=QMA1-XK | /SECONDARY
Cable_Id_1056 | =H9=JG1=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QMA1=XDC1-S1 | =K1=JK2+9+9F1-9F1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/BC017/BC018/BC028-1/SECONDARY
Cable_Id_1057 | =H5=HE1=UCA3=WDB1 | N2XH-Flex 0.6/1 kV 4G120mm² | =H5=HE1=UCA2-QB1 | =H5=HE1=UCA3-X1 | /B141/BC027
Cable_Id_1058 | =H6=HE1=UCA3=WDB1 | N2XH-Flex 0.6/1 kV 4G120mm² | =H6=HE1=UCA2-QB1 | =H6=HE1=UCA3-X1 | /B141/BC027
Cable_Id_1059 | =H9=JG1=QMA2=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QMA2=XDC1-S1 | =H9=JG1=QMA2-XK | /SECONDARY
Cable_Id_1060 | =H9=JG1=QMA2=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QMA2=XDC1-S1 | =K1=JK2+9+9E1-9E1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016
Cable_Id_1061 | =H9=JG1=QNA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QNA1=XDC1-S1 | =K1=JK2+8+8R1-8R1.XD1 | /DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_1062 | =H9=JG1=QNA1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG1=QNA1=XDC1-S1 | CTVZ-XK | /SECONDARY
Cable_Id_1063 | =H9=JG2=QMA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG2=QMA1=XDC1-S1 | =H9=JG2=QMA1-XK | /SECONDARY
Cable_Id_1064 | =H9=JG2=QMA1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG2=QMA1=XDC1-S1 | =K1=JK2+9+9D1-9D1.XD1 | /DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_1065 | =H9=JG2=QMA2=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG2=QMA2=XDC1-S1 | =H9=JG2=QMA2-XK | /SECONDARY
Cable_Id_1066 | =H9=JG2=QMA2=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=JG2=QMA2=XDC1-S1 | =K1=JK2+9+9G1-9G1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016
Cable_Id_1067 | =H9=KF1=GPB1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF1=GPB1=TAC1-B150.X531 | =H9=KF1=GPB1=MAA1 | /DFC007/DFC013/DFC014/C001/C101/C102/C104/C105-1/C008/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_1068 | =H9=KF1=GPB1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF1=GPB1=TAC1-X2 | =H9=KF1=GPB1=MAA1 | /DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/SECONDARY
Cable_Id_1069 | =H9=KF1=GPB1=MAA1=WDB2 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF1=GPB1=TAC1-X2 | =H9=KF1=GPB1=MAA1 | /DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/SECONDARY
Cable_Id_1070 | =H9=KF1=GPB1=MAA1=WDB3 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF1=GPB1=TAC1-X2 | =H9=KF1=GPB1=MAA1 | /DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/SECONDARY
Cable_Id_1071 | =H9=KF1=GPB1=TAC1=WDB5 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =H9=KF1=GPB1=TAC1-X390 | =K1=JK2+15-XD2 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB021
Cable_Id_1072 | =H9=KF1=QMA2=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF1=QMA2=XDC1-S1 | =H9=KF1=QMA2-XK | /SECONDARY
Cable_Id_1073 | =H9=KF1=QMA2=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF1=QMA2=XDC1-S1 | =K1=JK2+9+9R1-9R1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_1074 | =H9=KF2=GPB1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF2=GPB1=TAC1-B150.X531 | =H9=KF2=GPB1=MAA1 | /DFC008/DFC007/DFC013/DFC014/C001/C101/C102/C104/C105-1/C008/BC014/BC016/BC017/SECONDARY
Cable_Id_1075 | =H9=KF2=GPB1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF2=GPB1=TAC1-X2 | =H9=KF2=GPB1=MAA1 | /DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/SECONDARY
Cable_Id_1076 | =H9=KF2=GPB1=MAA1=WDB2 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF2=GPB1=TAC1-X2 | =H9=KF2=GPB1=MAA1 | /DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/SECONDARY
Cable_Id_1077 | =H9=KF2=GPB1=MAA1=WDB3 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF2=GPB1=TAC1-X2 | =H9=KF2=GPB1=MAA1 | /DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/SECONDARY
Cable_Id_1078 | =H9=KF2=GPB1=TAC1=WDB5 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =H9=KF2=GPB1=TAC1-X390 | =K1=JK2+15-XD2 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB021/DFB022/DFB023
Cable_Id_1079 | =H9=KF2=QMA2=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF2=QMA2=XDC1-S1 | =H9=KF2=QMA2-XK | /SECONDARY
Cable_Id_1080 | =H9=KF2=QMA2=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF2=QMA2=XDC1-S1 | =K1=JK2+9+9Q1-9Q1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/BC017/SECONDARY
Cable_Id_1081 | =H9=KF3=GPB1=MAA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =H9=KF3=GPB1=TAC1-B150.X531 | =H9=KF3=GPB1=MAA1 | /DFC008/DFC007/DFC013/DFC014/C001/C101/C102/C104/C105-1/C008/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_1082 | =H9=KF3=GPB1=MAA1=WDB1 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF3=GPB1=TAC1-X2 | =H9=KF3=GPB1=MAA1 | /DFV001/DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/VFD013/SECONDARY
Cable_Id_1083 | =H9=KF3=GPB1=MAA1=WDB2 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF3=GPB1=TAC1-X2 | =H9=KF3=GPB1=MAA1 | /DFV001/DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/VFD013/SECONDARY
Cable_Id_1084 | =H9=KF3=GPB1=MAA1=WDB3 | GAALFLEX®VFD 2XSLCH 4G95mm² | =H9=KF3=GPB1=TAC1-X2 | =H9=KF3=GPB1=MAA1 | /DFV001/DFV002/DFV003/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/VFD105/VFD010/VFD011/VFD012/VFD013/SECONDARY
Cable_Id_1085 | =H9=KF3=GPB1=TAC1=WDB5 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =H9=KF3=GPB1=TAC1-X390 | =K1=JK2+15-XD2 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB021/DFB022/DFB023/DFB024
Cable_Id_1086 | =H9=KF3=QMA2=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF3=QMA2=XDC1-S1 | =H9=KF3=QMA2-XK | /SECONDARY
Cable_Id_1087 | =H9=KF3=QMA2=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =H9=KF3=QMA2=XDC1-S1 | =K1=JK2+9+9P1-9P1.XD1 | /DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/BC014/BC016/SECONDARY
Cable_Id_1088 | =H5=HE1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+2-Q1 | =H5=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1089 | =H5=HE1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+2-Q1 | =H5=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1090 | =H5=HE1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+2-Q1 | =H5=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1091 | =H6=HE1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+3-Q1 | =H6=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1092 | =H6=HE1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+3-Q1 | =H6=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1093 | =H6=HE1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+3-Q1 | =H6=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/SECONDARY
Cable_Id_1094 | =H7=HE1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+4-Q1 | =H7=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/B142/SECONDARY
Cable_Id_1095 | =H7=HE1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+4-Q1 | =H7=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/B142/SECONDARY
Cable_Id_1096 | =H7=HE1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+4-Q1 | =H7=HE1=UCA2-QB1 | /DFB044/DFB043/B008/B139-1/B139-2/B139-3/B139-4/B139-5/B140-1/B140-2/B141/B141/B142/SECONDARY
Cable_Id_1097 | =H9=KF1=GPB1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+7-Q1 | =H9=KF1=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023/DFB022
Cable_Id_1098 | =H9=KF1=GPB1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+7-Q1 | =H9=KF1=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023/DFB022
Cable_Id_1099 | =H9=KF1=GPB1=TAC1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+7-Q1 | =H9=KF1=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023/DFB022
Cable_Id_1100 | =H9=KF2=GPB1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+8-Q1 | =H9=KF2=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023
Cable_Id_1101 | =H9=KF2=GPB1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+8-Q1 | =H9=KF2=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023
Cable_Id_1102 | =H9=KF2=GPB1=TAC1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+8-Q1 | =H9=KF2=GPB1=TAC1-X1 | /DFB025/DFB024/DFB023
Cable_Id_1103 | =H9=KF3=GPB1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+9-Q1 | =H9=KF3=GPB1=TAC1-X1 | /DFB025/DFB024
Cable_Id_1104 | =H9=KF3=GPB1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+9-Q1 | =H9=KF3=GPB1=TAC1-X1 | /DFB025/DFB024
Cable_Id_1105 | =H9=KF3=GPB1=TAC1=WDB3 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK1+9-Q1 | =H9=KF3=GPB1=TAC1-X1 | /DFB025/DFB024
Cable_Id_1106 | =H4=KF1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G25mm² | =K1=JK2+1+1D1-1D1.XD1 | =H4=KF1=TAC1-+07-XD01 | /DFB001/DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/BC026/BC023-1/BC023-2
Cable_Id_1107 | =H3=KF1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G25mm² | =K1=JK2+1+1G1-1G1.XD1 | =H3=KF1=TAC1-+07-XD01 | /DFB001/DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/BC026/BC023-1
Cable_Id_1108 | =H2=KF1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G25mm² | =K1=JK2+1+1J1-1J1.XD1 | =H2=KF1=TAC1-+07-XD01 | /DFB001/DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/BC025/BC022-2
Cable_Id_1109 | =H1=KF1=TAC1=WDB1 | N2XH-Flex 0.6/1 kV 5G25mm² | =K1=JK2+1+1M1-1M1.XD1 | =H1=KF1=TAC1-+07-XD01 | /DFB001/DFB002/DFB003/DFB004/DFB005/DFB006/DFB007/DFB008/DFB009/DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/BC025/BC022-1
Cable_Id_1110 | =E1=JJ2=GQA1=WDB1 | N2XH-Flex 0.6/1 kV 5G35mm² | =K1=JK2+4+4D1-4D1.XD1 | =E1=JA2=UCA1-X1 | /DFB005/DFB004/DFB003/DFB002/DFB001/DFB014/DFB015/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/B116/BC168/SECONDARY
Cable_Id_1111 | =E1=JJ1=GQA1=WDB1 | N2XH-Flex 0.6/1 kV 5G35mm² | =K1=JK2+4+4G1-4C1.XD1 | =E1=JA1=UCA1-X1 | /DFB005/DFB004/DFB003/DFB002/DFB001/DFB014/DFB015/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/BC167/SECONDARY
Cable_Id_1112 | =F1=HD1=GPB1=MAA1=WDB1 | N2XH-Flex 0.6/1 kV 5G25mm² | =K1=JK2+4+4M1-4M1.XD1 | =F1=HD1=GPB1=MAA1 | /DFB005/DFB004/DFB003/DFB002/DFB001/DFB014/DFB015/B001/B101/B102/B104-2/B105-1/B105-2/B004/B005/B006/B117/BC012/SECONDARY
Cable_Id_1113 | =TBA1=WDB1 | N2XH-Flex 0.6/1 kV 5G95mm² | =K1=JK2+8+8K1-8K1.XD1 | RENSEBYGVÆRK ROOMTBA_1-X1 | /DFB009/DFB010/DFB011/DFB012/DFB013/B008/BC158/BC174/LV_ROOM_CLIENT
Cable_Id_1114 | =H3=KC1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G16mm² | =K1=JK2+10+10G1-10G1.XD1 | =H3=KC1=UCA1-X1 | /DFB010/DFB011/DFB012/DFB013/B002/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/B123/BC134/SECONDARY
Cable_Id_1115 | =F2=KF4=GPB1=XDC3=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =K1=JK2+12-11D1.XD1 | =F2=KF4=GPB1=XDC3-S1 | /DFV006/DFV005/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/B105-2/B105-3/B115/B116/B144/B143/BC169
Cable_Id_1116 | =F2=KF3=GPB1=XDC3=WDB1 | GAALFLEX®VFD 2XSLCH 4G16mm² | =K1=JK2+12-11E1.XD1 | =F2=KF3=GPB1=XDC3-S1 | /DFV006/DFV005/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/B105-2/B105-3/B115/B116/B144/B143/B145/BC170
Cable_Id_1117 | =F2=KF2=GQA1=XDC1=WDB1 | GAALFLEX®VFD 2XSLCH 4G25mm² | =K1=JK2+12-11F1.XD1 | =F2=KF2=GQA1=XDC1-X1 | /DFV006/DFV005/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/B105-2/B105-3/B115/B116/B144/B143/B145/SECONDARY
Cable_Id_1118 | =F2=KF1=GQA1=XDC1=WDB1 | GAALFLEX®VFD 2XSLCH 4G25mm² | =K1=JK2+12-11H1.XD1 | =F2=KF1=GQA1=XDC1-X1 | /DFV006/DFV005/DFV004/VFD014/VFD101/VFD102/VFD103/VFD104/B105-2/B105-3/B115/B116/B144/B143/B145/SECONDARY
Cable_Id_1119 | =K1=JK2+13=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK2+13-AUX.XD0 | =K1=JK1+6-AUX.XD0 | /DFB043/DFB044
Cable_Id_1120 | =F1=HD1=HQB1=UCA1=WDB1 | N2XH-Flex 0.6/1 kV 5G2.5mm² | =K1=JK2+15-XD2 | =F1=HD1=HQB1=UCA1-X1 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-2/B105-1/B105-2/B004/B005/B006/B117/BC012/SECONDARY
Cable_Id_1121 | =H1=LC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H1=LC1=XDC1-XPH | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-1/B118/B119
Cable_Id_1122 | =H1=LC1=XDC2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H1=LC1=XDC2-XPH | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB042/B001/B101/B102/B104-1/B118/B119
Cable_Id_1123 | =H2=LC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H2=LC1=XDC1-XPH | /DFB043/B007/B107-1/B108/B120/B121
Cable_Id_1124 | =H2=LC1=XDC2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H2=LC1=XDC2-XPH | /DFB043/B007/B107-1/B108/B120/B121
Cable_Id_1125 | =H3=LC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H3=LC1=XDC1-XPH | /DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/B123
Cable_Id_1126 | =H3=LC1=XDC2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H3=LC1=XDC2-XPH | /DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/B123
Cable_Id_1127 | =H4=LC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H4=LC1=XDC1-XPH | /DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/B125
Cable_Id_1128 | =H4=LC1=XDC2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =H4=LC1=XDC2-XPH | /DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/B125
Cable_Id_1129 | =L1=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L1=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFBC002-1
Cable_Id_1130 | =L2=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L2=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFBC002-2
Cable_Id_1131 | =L3=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L3=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFBC003-1
Cable_Id_1132 | =L4=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L4=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFBC003-2
Cable_Id_1133 | =L5=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L5=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFBC001-2
Cable_Id_1134 | =L6=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK2+15-XD2 | =L6=LC1-X02 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/DFB019
Cable_Id_1135 | =K1=JK3=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+1-AUX.XD0 | =K1=JK2+15-XD2 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFBC004
Cable_Id_1136 | =H1=KF1=TAA1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU1.XD2 | =H1=KF1=TAA1-XT05 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/BC175/BC030/BC020/SECONDARY
Cable_Id_1137 | =H1=KF1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU1.XD2 | =H1=KF1=TAC1-07-XD01 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/BC175/BC030/BC020/SECONDARY
Cable_Id_1138 | =L1=JL1+1=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+1-HPU1.XD2 | =L1=JL1+1-X01 | /DFBC001-1/DFB020/B001/B101/B102/B104-1/B118/BC110/BC108/BC107
Cable_Id_1139 | =L1=JL2+1=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+1-HPU1.XD2 | =L1=JL2+1-X01 | /DFBC001-1/DFB020/B001/B101/B102/B104-1/B118/B119
Cable_Id_1140 | =L1=JL3+1=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+1-HPU1.XD2 | =L1=JL3+1-X01 | /DFBC001-1/DFB020/B001/B101/B102/B104-1/B118/B119
Cable_Id_1141 | =L1=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+1-HPU1.XD2 | =L1=LC1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFBC002-1
Cable_Id_1142 | =P1=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+1-HPU1.XD2 | =P1=LC1+1-=P2=LC1 | /DFBC001-1/DFB020/BC001/BC002/SECONDARY
Cable_Id_1143 | =H2=KF1=TAA1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU2.XD2 | =H2=KF1=TAA1-XT05 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/BC175/BC031/SECONDARY
Cable_Id_1144 | =H2=KF1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU2.XD2 | =H2=KF1=TAC1-07-XD01 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/BC175/BC031/SECONDARY
Cable_Id_1145 | =L2=JL1+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU2.XD2 | =L2=JL1+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B108/B120/BC124/BC122/BC121
Cable_Id_1146 | =L2=JL2+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU2.XD2 | =L2=JL2+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B108/B120/B121
Cable_Id_1147 | =L2=JL3+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+1-HPU2.XD2 | =L2=JL3+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B108/B120/B121
Cable_Id_1148 | =L2=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+1-HPU2.XD2 | =L2=LC1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFBC002-2
Cable_Id_1149 | =P1=LC1=WDB3 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+1-HPU2.XD2 | =P1=LC1+1-=P2=LC1 | /DFBC001-1/DFB020/BC001/BC002/SECONDARY
Cable_Id_1150 | =H9=KF1=GPB1=TAC1=WDB4 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =H9=KF1=GPB1=TAC1-X40 | /DFBC004/DFB021
Cable_Id_1151 | =H9=KF2=GPB1=TAC1=WDB4 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =H9=KF2=GPB1=TAC1-X40 | /DFBC004/DFB021/DFB022/DFB023
Cable_Id_1152 | =H9=KF3=GPB1=TAC1=WDB4 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =H9=KF3=GPB1=TAC1-X40 | /DFBC004/DFB021/DFB022/DFB023/DFB024
Cable_Id_1153 | =K1=JK1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =K1=JK1+6-AUX.XD0 | /DFBC004/DFB021/DFB022/DFB023/DFB024/DFB025
Cable_Id_1154 | =K1=JK2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =K1=JK2+13-AUX.XD0 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030
Cable_Id_1155 | =L5=JL1+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-COM.XD2 | =L5=JL1+1-X01 | /DFBC001-1/DFB020/B001/B101/B102/B104-2/B105-1/B105-2/B004/B005/B006/B117/BC012
Cable_Id_1156 | =L5=JL2+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-COM.XD2 | =L5=JL2+1-X01 | /DFBC001-1/DFB020/B001/B101/B102/B104-2/B105-1/B105-2/B105-3/B115/BC003/BC004/BC166-1
Cable_Id_1157 | =L5=JL3+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-COM.XD2 | =L5=JL3+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B140-1/BC019-1
Cable_Id_1158 | =L5=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =L5=LC1-X01 | /DFBC004/DFB040/DFB039/DFBC001-2
Cable_Id_1159 | =L6=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =L6=LC1-X01 | /DFBC004/DFB040/DFB041/DFB019
Cable_Id_1160 | =P1=LC1=WDB6 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | =P1=LC1+3-XD1 | /DFBC001-1/DFB020/BC001/BC002/SECONDARY
Cable_Id_1161 | =L6=KEA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | LOCAL CONTROL ROOM=L6=KEA1-X201 | /DFBC004/DFB040/DFB041/DFB019
Cable_Id_1162 | =L6=KEA1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-COM.XD2 | LOCAL CONTROL ROOM=L6=KEA1-X202 | /DFBC004/DFB040/DFB041/DFB019
Cable_Id_1163 | =H3=KF1=TAA1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-HPU3.XD2 | =H3=KF1=TAA1-XT05 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/B107-3/B107-4/BC176/BC034/BC021/SECONDARY
Cable_Id_1164 | =H3=KF1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-HPU3.XD2 | =H3=KF1=TAC1-07-XD01 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/B107-3/B107-4/BC176/BC034/BC021/SECONDARY
Cable_Id_1165 | =L3=JL2+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-HPU3.XD2 | =L3=JL2+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/B123
Cable_Id_1166 | =L3=JL3+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+2-HPU3.XD2 | =L3=JL3+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B111/B122/B123
Cable_Id_1167 | =L3=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-HPU3.XD2 | =L3=LC1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFBC003-1
Cable_Id_1168 | =P1=LC1=WDB4 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+2-HPU3.XD2 | =P1=LC1+2-XD1.1 | /DFBC001-1/DFB020/BC001/BC002/SECONDARY
Cable_Id_1169 | =H4=KF1=TAA1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+3-HPU4.XD2 | =H4=KF1=TAA1-XT05 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/B107-3/B107-4/BC176/BC035/SECONDARY
Cable_Id_1170 | =H4=KF1=TAC1=WDB2 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+3-HPU4.XD2 | =H4=KF1=TAC1-07-XD01 | /DFBC001-1/DFB020/B001/BC158/B107-1/B107-2/B107-3/B107-4/BC176/BC035/SECONDARY
Cable_Id_1171 | =L4=LC1=WDB2 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+3-HPU4.XD2 | =L4=LC1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFBC003-2
Cable_Id_1172 | =P1=LC1=WDB5 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =K1=JK3+3-HPU4.XD2 | =P1=LC1+2-XD1.2 | /DFBC001-1/DFB020/BC001/BC002/SECONDARY
Cable_Id_1173 | =TBA=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_1-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1174 | =TBA=WDB2 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_2-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1175 | =TBA=WDB3 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_3-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1176 | =TBA=WDB4 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_4-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1177 | =TBA=WDB5 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_5-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1178 | =TBA=WDB6 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_6-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1179 | =TBA=WDB7 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_7-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1180 | =TBA=WDB8 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_8-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1181 | =TBA=WDB9 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_9-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1182 | =TBA=WDB10 | N2XH-Flex 0.6/1 kV 3G4mm² | =K1=JK3+3-IT.XD2 | LV ROOM CLIENTTBA_10-X201 | /DFBC001-1/DFB020/BC001/BC174/LV_ROOM_CLIENT
Cable_Id_1183 | =L1=JL1+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L1=JL1+1-X01 | =L1=JL1+2-X01 | /BC107
Cable_Id_1184 | =H1=JF2=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L1=JL1+1-X230 | FIT =H1=JF2=BFA1 | /BC107/BC106/SECONDARY
Cable_Id_1185 | =H1=JG1=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L1=JL1+2-X10 | FIT =H1=JG1=BFA1 | /BC107/BC108/SECONDARY
Cable_Id_1186 | =H1=JF2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L1=JL1+2-X230 | AIT =H1=JF2=BQC1 | /BC107/BC106/SECONDARY
Cable_Id_1187 | =L1=JL2+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L1=JL2+1-X01 | =L1=JL2+2-X01 | /INTERNAL
Cable_Id_1188 | =H1=JG2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L1=JL2+2-X230 | UT =H1=JG2=BQC1 | /BC107/BC108/SECONDARY
Cable_Id_1189 | =L1=JL3+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L1=JL3+1-X01 | =L1=JL3+2-X01 | /INTERNAL
Cable_Id_1190 | =L2=JL1+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L2=JL1+1-X01 | =L2=JL1+2-X01 | /BC121
Cable_Id_1191 | =L2=JL2+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L2=JL2+1-X01 | =L2=JL2+2-X01 | /INTERNAL
Cable_Id_1192 | =L2=JL3+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L2=JL3+1-X01 | =L2=JL3+2-X01 | /INTERNAL
Cable_Id_1193 | =L3=JL1+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L3=JL1+1-X01 | =L3=JL1+2-X01 | /BC135
Cable_Id_1194 | =L3=JL2+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L3=JL2+1-X01 | =L3=JL2+2-X01 | /INTERNAL
Cable_Id_1195 | =L3=JL3+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L3=JL3+1-X01 | =L3=JL3+2-X01 | /INTERNAL
Cable_Id_1196 | =L4=JL1+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L4=JL1+1-X01 | =L4=JL1+2-X01 | /BC149
Cable_Id_1197 | =L4=JL2+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L4=JL2+1-X01 | =L4=JL2+2-X01 | /INTERNAL
Cable_Id_1198 | =L4=JL3+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L4=JL3+1-X01 | =L4=JL3+2-X01 | /INTERNAL
Cable_Id_1199 | =L5=JL1+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L5=JL1+1-X01 | =L5=JL1+2-X01 | /BC011/B117/BC012
Cable_Id_1200 | =L1=K3=JK3=WDB3 | N2XH-Flex 0.6/1 kV 5G35mm² | =K1=JK3+1-UPS3.XD0 | LV ROOM CLIENTTBA-X203 | /DFBC001-1/DFB020/B001/BC174/LV_ROOM_CLIENT
Cable_Id_1201 | =L4=JL2+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+3-HPU4.XD2 | =L4=JL2+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/B125
Cable_Id_1202 | =L4=JL3+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+3-HPU4.XD2 | =L4=JL3+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/B125
Cable_Id_1203 | =L4=JL1+1=WDB1 | N2XH-Flex 0.6/1 kV 3G6mm² | =K1=JK3+3-HPU4.XD2 | =L4=JL1+1-X01 | /DFBC004/DFB040/DFB039/DFB038/DFB037/DFB036/DFB035/DFB034/DFB033/DFB032/DFB031/DFB030/DFB043/B007/B107-1/B107-2/B107-3/B107-4/B107-5/B107-6/B107-7/B112/B114/B124/BC152/BC150/BC149
Cable_Id_1204 | =H9=JG2=BHA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL1+2-X230 | JQI =H9=JG2=BHA1 | /BC012/B117/B006/B005/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_1205 | =H9=JG2=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL1+1004-X1-AI | FT =H9=JG2=BFA1 | /BC012/B117/B006/B005/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_1206 | =L5=JL2+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L5=JL2+1-X01 | =L5=JL2+2-X01 | /INTERNAL
Cable_Id_1207 | =L5=JL3+2=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =L5=JL3+1-X01 | =L5=JL3+2-X01 | /INTERNAL
Cable_Id_1208 | =H1=JF3=BFA2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL3+1-X230 | FIT =H1=JF3=BFA1 | /BC019-1/B140-1/B107-5/B107-4/BC025/BC022-2/SECONDARY
Cable_Id_1209 | =H9=JG2=BFA2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL3+2-X230 | FIT =H9=JG2=BFA2 | /BC019-2/B140-2
Cable_Id_1210 | =N1=GMC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N1=GMC1=XDC1-=S1 | =N1=GMC1001-X1 | /SECONDARY
Cable_Id_1211 | =N1=GMC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N1=GMC1=XDC1-=S1 | LV ROOM CLIENTTBD-X1 | /SECONDARY
Cable_Id_1212 | =N2=GMC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N2=GMC1=XDC1-S1 | =N2=GMC1001-X1 | /SECONDARY
Cable_Id_1213 | =N2=GMC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N2=GMC1=XDC1-S1 | LV ROOM CLIENTTBD-X1 | /SECONDARY
Cable_Id_1214 | =N3=GMC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N3=GMC1=XDC1-S1 | =N3=GMC1001-X1 | /SECONDARY
Cable_Id_1215 | =N3=GMC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N3=GMC1=XDC1-S1 | LV ROOM CLIENTTBD-X1 | /SECONDARY
Cable_Id_1216 | =N4=GMC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N4=GMC1=XDC1-S1 | =N4=GMC1001-X1 | /SECONDARY
Cable_Id_1217 | =N4=GMC1=XDC1=WDB1 | N2XH-Flex 0.6/1 kV 5G70mm² | =N4=GMC1=XDC1-S1 | LV ROOM CLIENTTBD-X1 | /SECONDARY
Cable_Id_1218 | =P1=LC1=WDB1 | N2XH-Flex 0.6/1 kV 3G4mm² | =P1=LC1+1-=P2=LC1 | =K1=JK2+15-XD2 | /DFB030/DFB031/DFB032/DFB033/DFB034/DFB035/DFB036/DFB037/DFB038/DFB039/DFB040/DFB041/BC001/BC002
Cable_Id_1219 | =TBA_LVSGA=WGA1 | RE-2X(St)H 1x2x0.75mm² | HVSG-X11 | =K1=JK1+5-XD6 | /DFC010/DFC009/DFC008/DFC007/DFC013/SECONDARY
Cable_Id_1220 | =TBA_LVSGB=WGA1 | RE-2X(St)H 1x2x0.75mm² | HVSG-X12 | =K1=JK2-XD6 | /DFC010/DFC009/DFC008/DFC007/DFC013/DFC004-2/DFC011
Cable_Id_1221 | =H2=JF2=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L2=JL1+1-X230 | FIT =H2=JF2=BFA1 | /BC121/BC120/SECONDARY
Cable_Id_1222 | =H2=JG1=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L2=JL1+2-X10 | FIT =H2=JG1=BFA1 | /BC121/BC122/SECONDARY
Cable_Id_1223 | =H2=JF2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L2=JL1+2-X230 | AIT =H2=JF2=BQC1 | /BC121/BC120/SECONDARY
Cable_Id_1224 | =H2=JG2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L2=JL2+2-X230 | UT =H2=JG2=BQC1 | /BC121/BC122/SECONDARY
Cable_Id_1225 | =H2=JF3=BFA2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL3+1-X230 | FIT =H2=JF3=BFA1 | /BC019-1/B140-1/B107-5/B107-4/BC025/BC022-2/SECONDARY
Cable_Id_1226 | =H3=JF2=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L3=JL1+1-X230 | FIT =H3=JF2=BFA1 | /BC135/BC134/SECONDARY
Cable_Id_1227 | =H3=JG1=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L3=JL1+2-X10 | FIT =H3=JG1=BFA1 | /BC135/BC136/SECONDARY
Cable_Id_1228 | =H3=JF2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L3=JL1+2-X230 | AIT =H3=JF2=BQC1 | /BC135/BC134/SECONDARY
Cable_Id_1229 | =H3=JG2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L3=JL2+2-X230 | UT =H3=JG2=BQC1 | /BC135/BC136/SECONDARY
Cable_Id_1230 | =H3=JF3=BFA2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL3+1-X230 | FIT =H3=JF3=BFA1 | /BC019-1/B140-1/B107-6/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_1231 | =H4=JF2=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L4=JL1+1-X230 | FIT =H4=JF2=BFA1 | /BC149/BC148/SECONDARY
Cable_Id_1232 | =H4=JG1=BFA1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L4=JL1+2-X10 | FIT =H4=JG1=BFA1 | /BC149/BC150/SECONDARY
Cable_Id_1233 | =H4=JF2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L4=JL1+2-X230 | AIT =H4=JF2=BQC1 | /BC149/BC148/SECONDARY
Cable_Id_1234 | =H4=JG2=BQC1=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L4=JL2+2-X230 | UT =H4=JG2=BQC1 | /BC149/BC150/SECONDARY
Cable_Id_1235 | =H4=JF3=BFA2=WDB1 | N2XH-Flex 0.6/1 kV 3G2.5mm² | =L5=JL3+1-X230 | FIT =H4=JF3=BFA1 | /BC019-1/B140-1/B107-6/BC026/BC023-1/BC023-2/SECONDARY
Cable_Id_1236 | =H1=LC1=XDC1=WGA1 | Li02YCHXSHX[BK] 18x4 x 0.50mm² | =H1=LC1=XDC1-XT | =H1=LC1=UCA1-125XT......130XT | /DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C118/C119/C120/C121/C122
Cable_Id_1237 | =H1=LC1=XDC2=WGA2 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H1=LC1=XDC2-SMX7/1 | =H1=LC1=UCA1-121 SMX7/1 | /DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C118/C119/C120/C121/C122
Cable_Id_1238 | =H1=LC1=XDC2=WGA1 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H1=LC1=XDC2-SMX7/2 | =H1=LC1=UCA1-122 SMX7/2 | /DFC002/DFC001/DFC005/DFC006/C001/C101/C102/C118/C119/C120/C121/C122
Cable_Id_1239 | =H1=LC1=XDC1=WDB2 | HXSLCHXSHX 12 x 6mm² | =H1=LC1=UCA1-105XPA | =H1=LC1=XDC1-XPA | /DFB027/B007/BC158/B101/B102/B104-1/B118/B119
Cable_Id_1240 | =H1=LC1=XDC1=WGA2 | RE-2X(St)H 1x3x0.75mm² | =H1=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1241 | =H1=LC1=XDC1=WGA3 | RE-2X(St)H 1x3x0.75mm² | =H1=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1242 | =H1=LC1=XDC1=WDB4 | HXSLCHXSHX 12 x 6mm² | =H1=LC1=UCA1-105XPM | =H1=LC1=XDC1-XPM | /DFB027/B007/BC158/B101/B102/B104-1/B118/B119
Cable_Id_1243 | =H1=LC1=XDC2=WGA7 | RE-2X(St)H 1x3x0.75mm² | =H1=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1244 | =H1=LC1=XDC2=WGA8 | RE-2X(St)H 1x3x0.75mm² | =H1=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1245 | =H1=LC1=XDC1=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H1=LC1=XDC1-XG | /SECONDARY
Cable_Id_1246 | =H1=LC1=XDC1=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H1=LC1=XDC1-XG | /SECONDARY
Cable_Id_1247 | =H1=LC1=XDC2=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H1=LC1=XDC2-XG | /SECONDARY
Cable_Id_1248 | =H1=LC1=XDC2=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H1=LC1=XDC2-XG | /SECONDARY
Cable_Id_1249 | =H1=LC1=XDC1=BTA1=WGA1 | JZ-600 3G 1.5MM² | TSHL =H1=LC1=XDC1=BTA1 | =H1=LC1=XDC1-XPH | /SECONDARY
Cable_Id_1250 | =H1=LC1=XDC2=BTA2=WGA1 | JZ-600 3G 1.5MM² | TSHL =H1=LC1=XDC2=BTA2 | =H1=LC1=XDC2-XPH | /SECONDARY
Cable_Id_1251 | =H1=LC1=XDC1=WDB3 | HXSLCHXSHX 12 x 6mm² | =H1=LC1=XDC1-XPC | =H1=LC1=UCA1-105XPC | /DFB027/B007/BC158/B101/B102/B104-1/B118/B119
Cable_Id_1252 | =H1=HA2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA2=BTA2.3 | TIT =H1=HA2=BTA2.3 | /SECONDARY
Cable_Id_1253 | =H1=HA2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA2=BTA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1254 | =H1=HA2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA2=BTA2.2 | TIT =H1=HA2=BTA2.2 | /SECONDARY
Cable_Id_1255 | =H1=HA2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA2=BTA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_1256 | =H1=HA2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA2=BTA2.1 | TIT =H1=HA2=BTA2.1 | /SECONDARY
Cable_Id_1257 | =H1=HA2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA2=BTA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_1258 | =H1=HA2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA2=BTA1 | TIT =H1=HA2=BTA1 | /SECONDARY
Cable_Id_1259 | =H1=HA2=BPA2.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA2=BPA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1260 | =H1=HA2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA2=BPA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_1261 | =H1=HA2=BPA2.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA2=BPA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_1262 | =H1=HA2=BPA2.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA2=BPA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_1263 | =H1=HA2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=HA2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1264 | =H1=HA3=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA3=BTA1.2 | TIT =H1=HA3=BTA1.2 | /SECONDARY
Cable_Id_1265 | =H1=HA3=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA3=BTA1.1 | TIT =H1=HA3=BTA1.1 | /SECONDARY
Cable_Id_1266 | =H1=HA1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA1=BTA1.2 | TIT =H1=HA1=BTA1.2 | /SECONDARY
Cable_Id_1267 | =H1=HA1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA1=BTA1.1 | TIT =H1=HA1=BTA1.1 | /SECONDARY
Cable_Id_1268 | =H1=HA4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA4=BTA1 | TIT =H1=HA4=BTA1 | /SECONDARY
Cable_Id_1269 | =H1=HA4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA4=BTA2 | TIT =H1=HA4=BTA2 | /SECONDARY
Cable_Id_1270 | =H1=HA1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA1=BTA2 | TIT =H1=HA1=BTA2 | /SECONDARY
Cable_Id_1271 | =H1=HA5=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA5=BTA1 | TIT =H1=HA5=BTA1 | /SECONDARY/BC114/BC106/SECONDARY
Cable_Id_1272 | =H1=HA2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA2=BPC1 | =L1=JL3+1 | /C120/C119/C118/SECONDARY
Cable_Id_1273 | =H3=LC1=XDC2=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H3=LC1=XDC2-XG | /SECONDARY
Cable_Id_1274 | =H1=HA2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA2=BPA3 | =L1=JL3+2 | /C120/C119/C118/SECONDARY
Cable_Id_1275 | =H1=HA2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA2=BPC2 | =L1=JL3+2 | /C120/C119/C118/SECONDARY
Cable_Id_1276 | =H1=HA3=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA3=BTA1.2 | =L1=JL3+1 | /C120/C119/C118/SECONDARY
Cable_Id_1277 | =H1=HA3=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA3=BTA1.1 | =L1=JL3+1 | /C120/C119/C118/SECONDARY
Cable_Id_1278 | =H1=HA3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA3=BPA1 | =L1=JL3+2 | /SECONDARY/BC109/BC108/BC110/C120
Cable_Id_1279 | =H1=HA1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA1=BTA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1280 | =H1=HA1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA1=BTA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1281 | =H1=HA1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA1=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_1282 | =H1=HA1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA1=BPC2 | =L1=JL1+1 | /SECONDARY/BC109/BC108/BC107
Cable_Id_1283 | =H1=HA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA1=BPA1.2 | =L1=JL2+1 | /SECONDARY/BC107/BC106/C122
Cable_Id_1284 | =H1=HA1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA1=BPA2 | =L1=JL2+2 | /SECONDARY/BC107/BC106/C122
Cable_Id_1285 | =H1=HA4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA4=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1286 | =H1=HA4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA4=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_1287 | =H1=HA4=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA4=BPA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1288 | =H1=HA4=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA4=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1289 | =H1=HA4=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA4=BPA2 | =L1=JL1+2 | /SECONDARY/BC106/BC107
Cable_Id_1290 | =H1=HA5=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA5=BTA1 | =L1=JL2+2 | /SECONDARY/BC106/C122
Cable_Id_1291 | =H1=HA5=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA5=BPA1 | =L1=JL2+2 | /SECONDARY/BC106/C122
Cable_Id_1292 | =H1=HA5=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA5=BPA2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1293 | =H1=HA5=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA5=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1294 | =H1=KF1=GQB1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FT =H1=KF1=GQB1=BFA1 | =L1=JL1+2 | /SECONDARY/BC114/BC113/BC107
Cable_Id_1295 | =H1=HA2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1296 | =H1=HA2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA2=QNB1 | =L1=JL3+1 | /C120/C121/C122/BC106/BC114
Cable_Id_1297 | =H1=HA4=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA4=QNB1 | =L1=JL1+2 | /BC107/BC113/SECONDARY
Cable_Id_1298 | =H1=HA4=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA4=QNB1 | =L1=JL1+1 | /BC107/BC113/SECONDARY
Cable_Id_1299 | =H1=HA4=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=HA4=QNB1 | =L1=JL1+2 | /BC107/BC113/SECONDARY
Cable_Id_1300 | =H1=HA5=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA5=QNB1 | =L1=JL2+2 | /C122/BC106/BC114/SECONDARY
Cable_Id_1301 | =H1=HA5=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA5=QNB1 | =L1=JL2+1 | /C122/BC106/BC114/SECONDARY
Cable_Id_1302 | =H1=HA2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA2=BTA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_1303 | =H1=HA5=QNB1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | PY =H1=HA5=QNB1 | =L1=JL2+2 | /C122/BC106/BC114/SECONDARY
Cable_Id_1304 | =H1=HA1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA1=BPC1 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1305 | =H1=HA7=BTA1.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA7=BTA1.3 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1306 | =H1=HA7=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA7=BTA1.2 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1307 | =H1=HA7=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HA7=BTA1.1 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1308 | =H1=HA7=BTA1.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA7=BTA1.3 | TIT =H1=HA7=BTA1.3 | /SECONDARY
Cable_Id_1309 | =H1=HA7=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA7=BTA1.2 | TIT =H1=HA7=BTA1.2 | /SECONDARY
Cable_Id_1310 | =H1=HA7=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HA7=BTA1.1 | TIT =H1=HA7=BTA1.1 | /SECONDARY
Cable_Id_1311 | =H1=HA3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HA3=BPC1 | =L1=JL3+2 | /C120/BC110/BC108
Cable_Id_1312 | =H1=JF1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF1=BPA1.1 | =L1=JL1+1 | /BC107/BC108/SECONDARY
Cable_Id_1313 | =H1=JF1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF1=BPA1.2 | =L1=JL1+1 | /BC107/BC108/SECONDARY
Cable_Id_1314 | =H1=JF2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF2=BPA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1315 | =H1=JF2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF2=BPA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1316 | =H1=JF1=BPC1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JF1=BPC1.1 | =L1=JL2+1 | /C122/BC106/BC114/BC113/BC107/BC108/SECONDARY
Cable_Id_1317 | =H1=JF1=BPC1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JF1=BPC1.2 | =L1=JL2+1 | /C122/BC106/BC114/BC113/BC107/BC108/SECONDARY
Cable_Id_1318 | =H1=HC1=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =H1=HC1=BLA1 | =L1=JL1+2 | /BC107/BC108/SECONDARY
Cable_Id_1319 | =H1=HC1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HC1=BPA1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/SECONDARY
Cable_Id_1320 | =H1=HC1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HC1=BTA1.1 | =L1=JL2+1 | /C122/BC106/BC114/BC113/BC107/BC108/SECONDARY
Cable_Id_1321 | =H1=HC1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HC1=BTA1.2 | =L1=JL2+1 | /C122/BC106/BC114/BC113/BC107/BC108/SECONDARY
Cable_Id_1322 | =H1=HC1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HC1=BTA1.2 | TIT =H1=HC1=BTA1.2 | /SECONDARY
Cable_Id_1323 | =H1=HC1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HC1=BTA1.1 | TIT =H1=HC1=BTA1.1 | /SECONDARY
Cable_Id_1324 | =H1=HE1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HE1=BPA1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1325 | =F2=KF1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=KF1=BTA1 | TIT =F2=KF1=BTA1 | /SECONDARY
Cable_Id_1326 | =F2=KF1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=KF1=BTA1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/SECONDARY
Cable_Id_1327 | =F2=KF1=GQA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=KF1=GQA1=BPA1.1 | =F2=KF1=GQA1=XDC2-X7 | /INTERNAL
Cable_Id_1328 | =F2=KF1=GQA1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB1 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1329 | =F2=BTA4=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=BTA4 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1330 | =F2=BTA4=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=BTA4 | TIT =F2=BTA4 | /SECONDARY
Cable_Id_1331 | =F2=BPA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=BPA4 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1332 | =F2=KF2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=KF2=BTA1 | TIT =F2=KF2=BTA1 | /SECONDARY
Cable_Id_1333 | =F2=KF2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=KF2=BTA1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/SECONDARY
Cable_Id_1334 | =F2=QC3=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=QC3=BTA1 | TIT =F2=QC3=BTA1 | /BC171/BC163
Cable_Id_1335 | =F2=QC2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=QC2=BTA1 | TIT =F2=QC2=BTA1 | /BC172/SECONDARY
Cable_Id_1336 | =F2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =F2=BPC1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1337 | =F2=QC3=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=QC3=BTA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171
Cable_Id_1338 | =F2=QC3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=QC3=BPA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171
Cable_Id_1339 | =F2=QC3=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =F2=QC3=BLA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171/BC163/SECONDARY
Cable_Id_1340 | =F2=QC3=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC3=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162
Cable_Id_1341 | =F2=QC2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=QC2=BTA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172
Cable_Id_1342 | =F2=QC2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=QC2=BPA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172
Cable_Id_1343 | =F2=QC1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=QC1=BTA1 | TIT =F2=QC1=BTA1 | /BC173/SECONDARY
Cable_Id_1344 | =H1=JF2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF2=BTA2.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1345 | =H1=JF2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF2=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1346 | =H1=JF2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF2=BTA1 | TIT =H1=JF2=BTA1 | /BC106/SECONDARY
Cable_Id_1347 | =H1=JF2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF2=BTA2.1 | TIT =H1=JF2=BTA2.1 | /SECONDARY
Cable_Id_1348 | =H1=JF2=BQC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | AIT =H1=JF2=BQC1 | =L1=JL1+2 | /BC107/BC106/C122
Cable_Id_1349 | =H1=JF2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H1=JF2=BFB1 | =L1=JL1+2 | /BC107/BC106/C122
Cable_Id_1350 | =H1=JF2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=JF2=BFA1 | =L1=JL1+1 | /BC107/BC106/C122
Cable_Id_1351 | =H1=KC1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=KC1=BPC1 | =H1=KC1=UCA1X1-AI-X1-AI | /SECONDARY
Cable_Id_1352 | =F1=JF1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F1=JF1=BTA1 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1353 | =F1=JF1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F1=JF1=BTA2 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1354 | =F1=JF1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F1=JF1=BTA2 | TIT =F1=JF1=BTA2 | /SECONDARY
Cable_Id_1355 | =F1=JF1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F1=JF1=BTA1 | TIT =F1=JF1=BTA1 | /SECONDARY
Cable_Id_1356 | =F1=JF1=BPA1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F1=JF1=BPA1.3 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1357 | =H1=JG2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JG2=BPA1.1 | =L1=JL3+1 | /C120/BC110/BC108/BC109/SECONDARY
Cable_Id_1358 | =H1=JG2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JG2=BPA1.2 | =L1=JL3+1 | /C120/BC110/BC108/BC109/SECONDARY
Cable_Id_1359 | =H1=JG2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JG2=BTA1 | =L1=JL3+2 | /C120/BC110/SECONDARY
Cable_Id_1360 | =H1=JG2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JG2=BTA1 | TIT =H1=JG2=BTA1 | /SECONDARY/BC108/BC109/SECONDARY
Cable_Id_1361 | =H1=JG2=BQC1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | UT =H1=JG2=BQC1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1362 | =H1=JG2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JG2=BPC1 | =L1=JL3+2 | /C120/C119/C118/SECONDARY
Cable_Id_1363 | =H1=JG2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JG2=BPC2 | =L1=JL3+2 | /C120/BC110/BC108/BC109/SECONDARY
Cable_Id_1364 | =H1=JG2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H1=JG2=BFB1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1365 | =H1=JG2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JG2=QNA1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1366 | =H1=JG2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=JG2=QNA1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1367 | =H1=JG1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JG1=BPA1.2 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1368 | =H1=JG1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JG1=BPA1.1 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1369 | =H1=JG1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JG1=BPC1 | =L1=JL3+2 | /C120/BC110/SECONDARY
Cable_Id_1370 | =H1=JG1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=JG1=BFA1 | =L1=JL1+2 | /BC107/BC108/SECONDARY
Cable_Id_1371 | =H1=JG1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JG1=BPA2 | =L1=JL3+2 | /C120/BC110/SECONDARY
Cable_Id_1372 | =H1=JG1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JG1=BTA1 | =L1=JL3+2 | /C120/C119/C118/SECONDARY
Cable_Id_1373 | =H1=JG1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JG1=BTA1 | TIT =H1=JG1=BTA1 | /SECONDARY
Cable_Id_1374 | =H9=JG2=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=JG2=BTA1.1 | TIT =H9=JG2=BTA1.1 | /SECONDARY
Cable_Id_1375 | =H9=JG2=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=JG2=BTA1.2 | TIT =H9=JG2=BTA1.2 | /SECONDARY
Cable_Id_1376 | =H9=JG2=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H9=JG2=BTA1.1 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2
Cable_Id_1377 | =H9=JG2=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H9=JG2=BTA1.2 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2
Cable_Id_1378 | =H9=JG1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H9=JG1=BTA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_1379 | =H9=JG1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=JG1=BTA1 | TIT =H9=JG1=BTA1 | /SECONDARY
Cable_Id_1380 | =F1=HD1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TT =F1=HD1=BTA1 | =L5=JL1+1 | /BC011/C116/BC012/SECONDARY
Cable_Id_1381 | =F1=HD1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F1=HD1=BTA1 | TT =F1=HD1=BTA1 | /SECONDARY
Cable_Id_1382 | =F1=HD1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F1=HD1=BTA2 | TT =F1=HD1=BTA2 | /SECONDARY
Cable_Id_1383 | =F1=HD1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TT =F1=HD1=BTA2 | =L5=JL1+1 | /BC011/C116/BC012/SECONDARY
Cable_Id_1384 | =F1=HD1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F1=HD1=BPA1 | =L5=JL1+2 | /SECONDARY
Cable_Id_1385 | =F1=HD1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =F1=HD1=BPC1 | =L5=JL1+1 | /BC011/C116/BC012/SECONDARY
Cable_Id_1386 | =H1=JF3=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF3=BTA1 | TIT =H1=JF3=BTA1 | /SECONDARY
Cable_Id_1387 | =H1=JF3=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF3=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1388 | =H1=JF3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF3=BPA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1389 | =H1=JF3=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=JF3=BPA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1390 | =H1=JF3=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JF3=BPC2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1391 | =H1=JF3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=JF3=BPC1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1392 | =H1=JF3=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=JF3=BFA1 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1393 | =H1=JF4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF4=BTA1 | TIT =H1=JF4=BTA1 | /SECONDARY
Cable_Id_1394 | =H1=JF4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF4=BTA2 | TIT =H1=JF4=BTA2 | /SECONDARY/BC020/BC029
Cable_Id_1395 | =H1=JF4=BTA3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF4=BTA3 | TIT =H1=JF4=BTA3 | /SECONDARY/BC020/BC029
Cable_Id_1396 | =H1=JF4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF4=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1397 | =H1=JF4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF4=BTA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1398 | =H1=JF4=BTA3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF4=BTA3 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1399 | =H1=JF4=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF4=QNA1 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1400 | =H1=JF4=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1401 | =H1=JF4=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1402 | =H1=JF4=QNA2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1403 | =H1=JF4=QNA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF4=QNA2 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1404 | =F2=QC2=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC2=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1405 | =F2=QC1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC1=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/SECONDARY
Cable_Id_1406 | =F2=QC1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=QC1=BTA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC173
Cable_Id_1407 | =F2=QC1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=QC1=BPA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC173
Cable_Id_1408 | =F2=QC1=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =F2=QC1=BLA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC173/BC165/SECONDARY
Cable_Id_1409 | =H1=JF4=QNA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1410 | =H8=JF2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H8=JF2=BPA1 | =L5=JL3+2 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_1411 | =H9=JG2=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG2=BPA2 | =L5=JL3+1 | /SECONDARY
Cable_Id_1412 | =E1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =E1=BPA1.2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/SECONDARY
Cable_Id_1413 | =E1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =E1=BPA1.1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/SECONDARY
Cable_Id_1414 | =H1=JF2=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF2=QMA10 | =L1=JL2+2 | /C122/BC106
Cable_Id_1415 | =H1=HC2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H1=HC2=BPC1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1416 | =H1=HC2=BFA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=HC2=BFA3 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1417 | =H1=HC2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=HC2=BFA1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1418 | =H1=HC2=BFA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=HC2=BFA4 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1419 | =H1=HC2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=HC2=BTA1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1420 | =H1=HC2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=HC2=BTA1 | TIT =H1=HC2=BTA1 | /SECONDARY
Cable_Id_1421 | =H1=HC2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=HC2=BFA2 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1422 | =H1=HC2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=HC2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1423 | =H1=HC2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HC2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1424 | =H1=HC2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HC2=QNB1 | =L1=JL3+1 | /C120/C121/C122/BC106/BC114
Cable_Id_1425 | =H1=KF1=MAA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=KF1=MAA1=BPA1.1 | =L1=JL3+1 | /C120/C121/SECONDARY
Cable_Id_1426 | =H1=KF1=MAA1=BPA1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=KF1=MAA1=BPA1.3 | =L1=JL3+1 | /C120/C121/SECONDARY
Cable_Id_1427 | =H1=KF1=MAA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=KF1=MAA1=BPA1.2 | =L1=JL3+1 | /C120/C121/SECONDARY
Cable_Id_1428 | =H1=KF1=PZA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | XI =H1=KF1=PZA1 | =L1=JL3+2 | /C120/BC110/SECONDARY
Cable_Id_1429 | =H1=HA5=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA5=QMB1 | =L1=JL2+1 | /C122/BC106/BC114/SECONDARY
Cable_Id_1430 | =H1=HA5=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA5=QMB1 | =L1=JL2+1 | /C122/BC106/BC114/SECONDARY
Cable_Id_1431 | =H1=HA2=FLA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA2=FLA1 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1432 | =H1=HA2=FLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA2=FLA1 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1433 | =H1=HA7=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C118/C119/BC110/BC108/BC109/SECONDARY
Cable_Id_1434 | =H1=HA7=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C118/C119/BC110/BC108/BC109/SECONDARY
Cable_Id_1435 | =P1=LA1=BQB1=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA1=BQB1 | =P1=LA1=XDC1-FAI | /SECONDARY/C118/C119/BC110/BC109/SECONDARY
Cable_Id_1436 | =P1=LA1=BQB2=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA1=BQB2 | =P1=LA1=XDC1-FAI | /SECONDARY/C118/C119/SECONDARY
Cable_Id_1437 | =P1=LA1=BQB3=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA1=BQB3 | =P1=LA1=XDC1-FAI | /SECONDARY/C118/C119/BC110/BC108/BC107/SECONDARY
Cable_Id_1438 | =P1=LA1=BQB4=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA1=BQB4 | =P1=LA1=XDC1-FAI | /SECONDARY/C118/C119/C120/SECONDARY
Cable_Id_1439 | =P1=LA5=BQB1=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA5=BQB1 | =P1=LA5=XDC1-FAI | /SECONDARY/BC167/C004/BC003/BC177/SECONDARY
Cable_Id_1440 | =P1=LA5=BQB2=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA5=BQB2 | =P1=LA5=XDC1-FAI | /SECONDARY/BC167/C004/BC003/BC004/BC177/BC178/BC179/SECONDARY
Cable_Id_1441 | =P1=LA5=BQB3=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA5=BQB3 | =P1=LA5=XDC1-FAI | /SECONDARY/BC167/C005/C011/C141/C142/BC170
Cable_Id_1442 | =P1=LA5=BQB4=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA5=BQB4 | =P1=LA5=XDC1-FAI | /SECONDARY/BC167/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1443 | =P1=LA7=BQB2=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA7=BQB2 | =P1=LA6=XDC1-FAI | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1444 | =P1=LA7=BQB1=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA7=BQB1 | =P1=LA6=XDC1-FAI | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C107-6/BC026/BC023-1/SECONDARY
Cable_Id_1445 | =P1=LA8=BQB2=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA8=BQB2 | =P1=LC1-X6-FAI | /BC001/BC002/DFC014/DFC013/DFC007/SECONDARY
Cable_Id_1446 | =P1=LA8=BQB1=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA8=BQB1 | =P1=LC1-X6-FAI | /BC001/BC002/DFC014/DFC013/DFC007/DFC008/DFC009/DFC010/DFC004-2/SECONDARY
Cable_Id_1447 | =H1=JF2=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H1=JF2=BLB1 | =L1=JL2+2
Cable_Id_1448 | =H1=JF1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H1=JF1=BLB1 | =L1=JL1+2
Cable_Id_1449 | =H1=HC1=QMA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_1450 | =H1=HC1=QMA4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_1451 | =H1=HA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H1=HA1=BPA1.1 | =L1=JL2+1 | /C122/BC106/BC107/SECONDARY
Cable_Id_1452 | =H1=JF1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF1=QMB1 | =L1=JL1+2 | /BC107/BC106/SECONDARY
Cable_Id_1453 | =H1=JF1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF1=QMB1 | =L1=JL1+2 | /BC107/BC106/SECONDARY
Cable_Id_1454 | =H1=HC2=QNB2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HC2=QNB2 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114/SECONDARY
Cable_Id_1455 | =H1=HC2=QNB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HC2=QNB2 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114/SECONDARY
Cable_Id_1456 | =H9=JG1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG1=BPA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_1457 | =F2=EBB1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=EBB1=BTA2 | =F2=EBB1=UCA1-X15 | /SECONDARY/BC168/C011/C141/BC169
Cable_Id_1458 | =F2=QC3=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC3=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162
Cable_Id_1459 | =F2=QC3=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC3=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162
Cable_Id_1460 | =F2=QC2=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC2=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1461 | =F2=QC1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC1=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1462 | =F2=QC1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC1=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC173
Cable_Id_1463 | =F2=QC2=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC2=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172
Cable_Id_1464 | =F2=QC2=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC2=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1465 | =F2=QC1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC1=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC173
Cable_Id_1466 | =F2=QC1=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC1=QMA1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1467 | =F2=KF2=QMB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF2=QMB3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1468 | =F2=KF2=QMB3=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF2=QMB3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1469 | =F2=KF1=QMB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF1=QMB3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1470 | =F2=KF1=QMB3=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF1=QMB3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1471 | =F2=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/BC168/SECONDARY
Cable_Id_1472 | =F2=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/BC168/SECONDARY
Cable_Id_1473 | =F2=BTA3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=BTA3 | =F2=EBB1=UCA1-X15 | /SECONDARY/BC168/C011/C141/BC169
Cable_Id_1474 | =F2=EBB1=BTA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | TSH =F2=EBB1=BTA1 | =F2=EBB1=UCA1-X15 | /SECONDARY/BC168/C011/C141/BC169
Cable_Id_1475 | =H9=JG1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG1=BPA2 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_1476 | =H1=HA2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=HA2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1477 | =H1=HA5=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=HA5=QNB1 | =L1=JL2+2 | /C122/BC106/BC114/SECONDARY
Cable_Id_1478 | =H1=HA4=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=HA4=QNB1 | =L1=JL1+2 | /BC107/BC113/SECONDARY
Cable_Id_1479 | =H1=HC2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=HC2=QNB1 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114
Cable_Id_1480 | =H1=JG2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=JG2=QNA1 | =L1=JL2+2 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1481 | =H1=JF4=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1482 | =H1=JF4=QNA2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-2/SECONDARY
Cable_Id_1483 | =H9=JG1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=JG1=BTA2 | TIT =H9=JG1=BTA2 | /SECONDARY
Cable_Id_1484 | =H9=JG1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H9=JG1=BTA2 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_1485 | =F1=HD1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =F1=HD1=BPC2 | =L5=JL1+2 | /BC012/SECONDARY
Cable_Id_1486 | =H9=JG2=BTA2=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | TE =H9=JG2=BTA2 | JQI =H9=JG2=BHA1 | /SECONDARY/BC028-2/SECONDARY
Cable_Id_1487 | =H9=JG1=BTA3=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | TE =H9=JG1=BTA3 | JQI =H9=JG2=BHA1 | /SECONDARY
Cable_Id_1488 | =H9=KF1=GPB1=BTA5.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF3=GPB1=BTA5.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1489 | =H9=KF1=GPB1=BTA4.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF3=GPB1=BTA4.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1490 | =H9=KF1=GPB1=BTA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | TE =H9=KF3=GPB1=BTA1.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1491 | =H9=KF1=GPB1=BTA3.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF3=GPB1=BTA3.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1492 | =H9=KF1=GPB1=BTA2.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | TE =H9=KF3=GPB1=BTA2.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1493 | =H9=KF2=GPB1=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF2=GPB1=BTA2.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1494 | =H9=KF2=GPB1=BTA3.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF2=GPB1=BTA3.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1495 | =H9=KF2=GPB1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF2=GPB1=BTA1.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1496 | =H9=KF2=GPB1=BTA4.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF2=GPB1=BTA4.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1497 | =H9=KF2=GPB1=BTA5.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF2=GPB1=BTA5.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1498 | =H9=KF3=GPB1=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF1=GPB1=BTA2.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1499 | =H9=KF3=GPB1=BTA3.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF1=GPB1=BTA3.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1500 | =H9=KF3=GPB1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF1=GPB1=BTA1.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1501 | =H9=KF3=GPB1=BTA4.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF1=GPB1=BTA4.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1502 | =H9=KF3=GPB1=BTA5.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H9=KF1=GPB1=BTA5.1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1503 | =H1=JF3=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=JF3=BFA2 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1504 | =H1=HA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HA1=QMB1 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1505 | =H1=HA1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HA1=QMB1 | =L1=JL1+1 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1506 | =H1=HE1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=HE1=QMA1 | =L1=JL1+1 | /BC107/SECONDARY
Cable_Id_1507 | =H1=HE1=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=HE1=QMA1 | =L1=JL1+1 | /BC107/SECONDARY
Cable_Id_1508 | =H1=HC2=QNB2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=HC2=QNB2 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114/SECONDARY
Cable_Id_1509 | =H1=JF2=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF2=QMA10 | =L1=JL2+2 | /C122/BC106
Cable_Id_1510 | =H1=JG2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JG2=QNA1 | =L1=JL2+1 | /C122/BC106/BC114/BC113/BC107/BC108/BC109/SECONDARY
Cable_Id_1511 | =H1=HC2=QNB2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=HC2=QNB2 | =L1=JL3+2 | /C120/C121/C122/BC106/BC114/SECONDARY
Cable_Id_1512 | =H9=JG2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FT =H9=JG2=BFA1 | JQI =H9=JG2=BHA1 | /BC028-2/SECONDARY
Cable_Id_1513 | =H1=HC1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =H1=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1514 | =F1=JF1=BQC1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | AT =F1=JF1=BQC1.1 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1515 | =F1=JF1=BQC1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | AT =F1=JF1=BQC1.2 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1516 | =F1=JF1=BQC1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | AT =F1=JF1=BQC1.3 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1517 | =H9=JG2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG2=BPA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2
Cable_Id_1518 | =H9=KF3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF3=BPC1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1519 | =H9=KF2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF2=BPC1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1520 | =H9=KF1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF1=BPC1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1521 | =H9=KF1=GPB1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF3=GPB1=BPC1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1522 | =H9=KF2=GPB1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF2=GPB1=BPC1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1523 | =H9=KF3=GPB1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H9=KF1=GPB1=BPC1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1524 | =H9=KF1=GPB1=BSG1=WGA1 | RE-2X(St)H 1x2x0.75mm² | VT =H9=KF3=GPB1=BSG1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1525 | =H9=KF2=GPB1=BSG1=WGA1 | RE-2X(St)H 1x2x0.75mm² | VT =H9=KF2=GPB1=BSG1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1526 | =H9=KF3=GPB1=BSG1=WGA1 | RE-2X(St)H 1x2x0.75mm² | VT =H9=KF1=GPB1=BSG1 | =L5=JL1+2 | /INTERNAL
Cable_Id_1527 | =F2=KF1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF1=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1528 | =F2=QMB9=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMB9 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1529 | =F2=QMB9=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMB9 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1530 | =F2=QMB7=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMB7 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1531 | =F2=QMB7=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMB7 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1532 | =F2=QMB6=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMB6 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1533 | =F2=QMB6=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMB6 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006
Cable_Id_1534 | =F2=QMB8=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMB8 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1535 | =F2=QMB8=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMB8 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1536 | =F2=QC3=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC3=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171
Cable_Id_1537 | =F2=QC3=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC3=QMB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171
Cable_Id_1538 | =F2=KF2=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF2=QMB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1539 | =P1=LA6=BQB2=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA6=BQB2 | =P1=LA6=XDC1-FAI | /SECONDARY/BC027/C139
Cable_Id_1540 | =P1=LA6=BQB1=WGA1 | RE-2X(St)H 1x3x0.75mm² | AT =P1=LA6=BQB1 | =P1=LA6=XDC1-FAI | /SECONDARY/BC027/C140/C140
Cable_Id_1541 | =P1=LA1=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA1=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C102/C118/SECONDARY
Cable_Id_1542 | =P1=LA5=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA5=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C102/C104/C105-1/C105-2/C004/BC167/SECONDARY
Cable_Id_1543 | =P1=LA6=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA6=XDC1-FAI | =P1=LC1-X6-FAI | /BC002/BC001/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/C138-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1544 | =F2=KF3=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LS =F2=KF3=BLB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/BC169
Cable_Id_1545 | =F2=BTA5=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=BTA5 | TIT =F2=BTA5 | /SECONDARY
Cable_Id_1546 | =F2=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=BTA2 | TIT =F2=BTA2 | /BC170/SECONDARY
Cable_Id_1547 | =F2=KF1=GQA1=BLB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB2 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1548 | =F2=KF2=GQA1=BLB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB2 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1549 | =F2=KF2=GQA1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB1 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1550 | =F2=KF2=GQA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=KF2=GQA1=BPA1.1 | =F2=KF2=GQA1=XDC2-X5 | /INTERNAL
Cable_Id_1551 | =P1=LA6=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA6=XDC1-FAI | =P1=LC1-X6-FAI | /BC002/BC001/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/C138-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1552 | =P1=LA1=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA1=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C102/C118/SECONDARY
Cable_Id_1553 | =P1=LA5=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =P1=LA5=XDC1-FAI | =P1=LC1-XD2 | /BC002/BC001/C001/C101/C102/C104/C105-1/C105-2/C004/BC167/SECONDARY
Cable_Id_1554 | =H8=JF1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H8=JF1=BPC1 | =L5=JL3+1 | /BC019-2/C138-3/C139/SECONDARY
Cable_Id_1555 | =H8=JF1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H8=JF1=BPC2 | =L5=JL3+1 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_1556 | =H8=JF1=BPC3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H8=JF1=BPC3 | =L5=JL3+1 | /BC019-2/C138-3/C139/C140/C140/SECONDARY
Cable_Id_1557 | =H5=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H5=BPC1 | =L5=JL3+1 | /BC019-2/C138-3/C139/SECONDARY
Cable_Id_1558 | =H6=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H6=BPC1 | =L5=JL3+1 | /BC019-2/C138-3/C139/C140/SECONDARY
Cable_Id_1559 | =H7=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H7=BPC1 | =L5=JL3+1 | /BC019-2/C138-3/C139/C140/C140/SECONDARY
Cable_Id_1560 | =H9=JG2=BPA3.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG2=BPA3.1 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2
Cable_Id_1561 | =H1=JF1=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF1=QMA10 | =L1=JL1+2 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1562 | =H1=JF1=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF1=QMA10 | =L1=JL1+2 | /BC107/BC108/BC109/SECONDARY
Cable_Id_1563 | =H1=JF2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF2=BTA2.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1564 | =H1=JF2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF2=BTA2.2 | TIT =H1=JF2=BTA2.2 | /SECONDARY
Cable_Id_1565 | =H1=JF2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H1=JF2=BTA2.3 | =L1=JL1+1 | /SECONDARY
Cable_Id_1566 | =H1=JF2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H1=JF2=BTA2.3 | TIT =H1=JF2=BTA2.3 | /SECONDARY
Cable_Id_1567 | =F1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F1=BLB1 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1568 | =H9=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H9=BLB1 | =L5=JL1+2
Cable_Id_1569 | =P1=LA6=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA6=PZA1 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/SECONDARY
Cable_Id_1570 | =P1=LA7=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA7=PZA1 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C107-6/BC026/BC023-1/SECONDARY
Cable_Id_1571 | =F2=BTA5=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=BTA5 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1572 | =F2=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=BTA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1573 | =F2=QC3=QMB4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC3=QMB4 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC163/SECONDARY
Cable_Id_1574 | =F2=QC3=QMB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC3=QMB4 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC163/SECONDARY
Cable_Id_1575 | =F2=QC2=QMB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC2=QMB4 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC164/SECONDARY
Cable_Id_1576 | =F2=QC2=QMB4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC2=QMB4 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC164/SECONDARY
Cable_Id_1577 | =F2=QC1=QMB4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC1=QMB4 | =L5=JL2+1 | /BC166-1/BC004/BC003/BC177/SECONDARY
Cable_Id_1578 | =F2=QC1=QMB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QC1=QMB4 | =L5=JL2+1 | /BC166-1/BC004/BC003/BC177/SECONDARY
Cable_Id_1579 | =F2=JA1=QMB9=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=JA1=QMB9 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1580 | =F2=JA1=QMB9=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=JA1=QMB9 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1581 | =F2=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/BC160-2/BC161/BC162/SECONDARY
Cable_Id_1582 | =F2=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/BC160-2/BC161/BC162/SECONDARY
Cable_Id_1583 | =F2=KF3=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF3=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC169
Cable_Id_1584 | =F2=KF3=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF3=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC169
Cable_Id_1585 | =F2=KF3=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF3=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC169
Cable_Id_1586 | =F2=KF3=QMA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF3=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC169
Cable_Id_1587 | =F2=KF4=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF4=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC170
Cable_Id_1588 | =F2=KF4=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF4=QMA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC170
Cable_Id_1589 | =F2=KF4=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=KF4=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC170
Cable_Id_1590 | =F2=KF4=QMA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=KF4=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/BC170
Cable_Id_1591 | =F2=QMA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMA4 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1592 | =F2=QMA4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMA4 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1593 | =F2=QMA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1594 | =F2=QMA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMA2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1595 | =F2=QMA5=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMA5 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1596 | =F2=QMA5=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMA5 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1597 | =F2=QMA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =F2=QMA3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1598 | =F2=QMA3=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QMA3 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1599 | =P1=LA7=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA7=PZA2 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1600 | =P1=LA8=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA8=PZA1 | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106
Cable_Id_1601 | =P1=LA9=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA9=PZA1 | =P1=LA9=XDC1-X1 | /C107-1/C106/C101/C102/C104/C105-1/C105-2/SECONDARY
Cable_Id_1602 | =P1=LA9=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA9=PZA2 | =P1=LA9=XDC1-X1 | /C107-1/C106/C101/SECONDARY
Cable_Id_1603 | =P1=LA9=PZA3=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA9=PZA3 | =P1=LA9=XDC1-X1 | /C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C114/SECONDARY
Cable_Id_1604 | =P1=LA1=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA1=PZA1 | =P1=LA1=XDC1-FDO | /SECONDARY/C118/SECONDARY
Cable_Id_1605 | =P1=LA1=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA1=PZA2 | =P1=LA1=XDC1-FDO | /SECONDARY/C118/C119/SECONDARY
Cable_Id_1606 | =P1=LA5=PZA1=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA5=PZA1 | =P1=LA5=XDC1-FDO | /SECONDARY/BC167/C004/SECONDARY
Cable_Id_1607 | =P1=LA5=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA5=PZA2 | =P1=LA5=XDC1-FDO | /SECONDARY/BC167/C005/SECONDARY
Cable_Id_1608 | =P1=LA6=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA6=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/C138-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1609 | =P1=LA1=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA1=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C102/C118/SECONDARY
Cable_Id_1610 | =P1=LA1=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA1=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C102/C118/SECONDARY
Cable_Id_1611 | =P1=LA5=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA5=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C102/C104/C105-1/C105-2/C004/BC167/SECONDARY
Cable_Id_1612 | =P1=LA5=XDC1=WGA3 | CTS-CHZ 5x0.75mm² | =P1=LA5=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C102/C104/C105-1/C105-2/C004/BC167/SECONDARY
Cable_Id_1613 | =P1=LA6=XDC1=WGA4 | CTS-CHZ 5x0.75mm² | =P1=LA6=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/C138-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1614 | =P1=LA6=XDC1=WGA5 | CTS-CHZ 5x0.75mm² | =P1=LA6=XDC1-FDO | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C107-1/C107-2/C107-3/C107-4/C107-5/C138-1/C138-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1615 | =P1=LA9=XDC1=WGA1 | CTS-CHZ 5x0.75mm² | =P1=LA9=XDC1-X1 | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C107-1/SECONDARY
Cable_Id_1616 | =P1=LA9=XDC1=WGA2 | CTS-CHZ 5x0.75mm² | =P1=LA9=XDC1-X1 | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106/C107-1/SECONDARY
Cable_Id_1617 | =H1=JF2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF2=QNA1 | =L1=JL3+2 | /C120/C121/SECONDARY
Cable_Id_1618 | =H1=JF2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H1=JF2=QNA1 | =L1=JL3+2 | /C120/C121/SECONDARY
Cable_Id_1619 | =H1=JF2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H1=JF2=QNA1 | =L1=JL3+2 | /C120/C121/SECONDARY
Cable_Id_1620 | =H1=JF2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H1=JF2=QNA1 | =L1=JL3+2 | /BC107/BC106/C122/SECONDARY
Cable_Id_1621 | =F2=KF2=GQA1=CMA3=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=CMA3=QMA1 | =F2=KF2=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1622 | =F2=KF2=GQA1=CMA2=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=CMA2=QMA1 | =F2=KF2=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1623 | =F2=KF2=GQA1=CMA1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=CMA1=QMA1 | =F2=KF2=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1624 | =F2=KF2=GQA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=QMB1 | =F2=KF2=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1625 | =F2=KF1=GQA1=CMA3=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=CMA3=QMA1 | =F2=KF1=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1626 | =F2=KF1=GQA1=CMA2=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=CMA2=QMA1 | =F2=KF1=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1627 | =F2=KF1=GQA1=CMA1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=CMA1=QMA1 | =F2=KF1=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1628 | =F2=KF1=GQA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=QMB1 | =F2=KF1=GQA1=XDC2-X2 | /INTERNAL
Cable_Id_1629 | =F2=KF1=GQA1=BLB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB3 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1630 | =F2=KF2=GQA1=BLB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB3 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1631 | =F2=KF1=GQA1=BSE1=WGA1 | RE-2X(St)H 1x3x0.75mm² | SE =F2=KF1=GQA1=BSE1 | =F2=KF1=GQA1=XDC2-X4 | /INTERNAL
Cable_Id_1632 | =F2=KF2=GQA1=BSE1=WGA1 | RE-2X(St)H 1x3x0.34mm² | SE =F2=KF2=GQA1=BSE1 | =F2=KF2=GQA1=XDC2-X4 | /INTERNAL
Cable_Id_1633 | =F2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =F2=BFA2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1634 | =F2=JA1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=JA1=BPA1 | =L5=JL2+1
Cable_Id_1635 | =H9=JG1=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG1=BPA3 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1/SECONDARY
Cable_Id_1636 | =F2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =F2=BTA1 | TIT =F2=BTA1 | /SECONDARY
Cable_Id_1637 | =F2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=BPA1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1638 | =H9=JG2=BPA3.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=JG2=BPA3.2 | =L5=JL1+1 | /BC011/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2/SECONDARY
Cable_Id_1639 | =F2=JF2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F2=JF2=BPA1 | =L5=JL2+1 | /BC166-1/BC004/BC177/BC178
Cable_Id_1640 | =F2=QC1=QMB6=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC1=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/SECONDARY
Cable_Id_1641 | =F2=QC1=QMB6=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC1=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/SECONDARY
Cable_Id_1642 | =F2=QC2=QMB6=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC2=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/BC178/SECONDARY
Cable_Id_1643 | =F2=QC2=QMB6=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC2=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/BC178/SECONDARY
Cable_Id_1644 | =F2=QC3=QMB6=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =F2=QC3=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/BC178/BC179/SECONDARY
Cable_Id_1645 | =F2=QC3=QMB6=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=QC3=QMB6 | =L5=JL2+1 | /BC166-1/BC004/BC177/BC178/BC179/SECONDARY
Cable_Id_1646 | =P1=LA1=PZA3=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA1=PZA3 | =P1=LA1=XDC1-FDO | /SECONDARY/C118/C119/C120/C121/SECONDARY
Cable_Id_1647 | =P1=LA1=PZA4=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA1=PZA4 | =P1=LA1=XDC1-FDO | /SECONDARY/C118/C119/BC110/SECONDARY
Cable_Id_1648 | =P1=LA6=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA6=PZA2 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/SECONDARY
Cable_Id_1649 | =P1=LA6=PZA3=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA6=PZA3 | =P1=LA6=XDC1-FDO | /BC027
Cable_Id_1650 | =P1=LA6=PZA4=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA6=PZA4 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C107-6/C107-7
Cable_Id_1651 | =P1=LA6=PZA5=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA6=PZA5 | =P1=LA6=XDC1-FDO | /SECONDARY/BC027/C139/C138-3/C138-2/C138-1/C107-6/C107-7/SECONDARY
Cable_Id_1652 | =F2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =F2=BPC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1653 | =F2=KF4=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LS =F2=KF4=BLB1 | =L5=JL2+1 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1654 | =F2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =F2=BTA1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/SECONDARY
Cable_Id_1655 | =P1=LA5=PZA4=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA5=PZA4 | =P1=LA5=XDC1-FDO | /SECONDARY/BC167/C004/BC003/BC004/BC160-2/BC161/BC162/SECONDARY
Cable_Id_1656 | =F2=QC3=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =F2=QC3=BFB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/BC179/SECONDARY
Cable_Id_1657 | =F2=QC2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =F2=QC2=BFB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/BC177/BC178/SECONDARY
Cable_Id_1658 | =F2=QC1=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =F2=QC1=BFB1 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/BC177/SECONDARY
Cable_Id_1659 | =P1=LA8=PZA2=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA8=PZA2 | =P1=LC1-X8-FDO | /BC002/BC001/C001/C101/C106
Cable_Id_1660 | =P1=LA8=PZA3=WGA1 | CTS-CHZ 5x0.75mm² | -=P1=LA8=PZA3 | =P1=LC1-X8-FDO | /BC002/BC001/C001/SECONDARY
Cable_Id_1661 | =H1=JF2=QMA6=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H1=JF2=QMA6 | =L1=JL1+2 | /SECONDARY
Cable_Id_1662 | =H1=HA4=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H1=HA4=BFA1 | =L1=JL1+2 | /C122/BC106/BC114/SECONDARY
Cable_Id_1663 | =SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =SJB3 | =L5=JL3+1 | /BC019-2/C138-3/C139/BC027
Cable_Id_1664 | =H1=SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=SJB6 | =L1=JL1+1 | /C120/BC110/BC109/SECONDARY
Cable_Id_1665 | =SJB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =SJB4 | =L5=JL3+1 | /BC019-2/C138-3/C139/BC027/SECONDARY
Cable_Id_1666 | =SJB5=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =SJB5 | =L5=JL3+1 | /BC019-2/C138-3/C139/SECONDARY
Cable_Id_1667 | =SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =SJB2 | =L5=LC1-XFSDI
Cable_Id_1668 | =F1=HD1=GPB1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =F1=HD1=GPB1=SJB1 | =L5=JL1+1 | /BC011/C116/BC012/SECONDARY
Cable_Id_1669 | =H9=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H9=SJB1 | =L5=JL1+1 | /SECONDARY
Cable_Id_1670 | =H9=KF3=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H9=KF3=SJB1 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/SECONDARY
Cable_Id_1671 | =H9=KF2=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H9=KF2=SJB1 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/BC017/SECONDARY
Cable_Id_1672 | =H9=KF1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H9=KF1=SJB1 | =L5=JL1+1 | /BC011/C010/C009/BC014/BC016/BC017/BC018/SECONDARY
Cable_Id_1673 | =H1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=SJB4 | =L1=JL2+1 | /C120/C121/SECONDARY
Cable_Id_1674 | =L5=JL2=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =L5=JL2=SJB1 | =L5=JL2+1 | /BC166-1/SECONDARY
Cable_Id_1675 | =L5=JL2=SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =L5=JL2=SJB2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/C006/SECONDARY
Cable_Id_1676 | =L5=JL2=SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =L5=JL2=SJB3 | =L5=JL2+1 | /BC166-1/BC004/BC177/SECONDARY
Cable_Id_1677 | =F2=KF1=GQA1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =F2=KF1=GQA1=SJB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/SECONDARY
Cable_Id_1678 | =F2=KF2=GQA1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =F2=KF2=GQA1=SJB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/SECONDARY
Cable_Id_1679 | =H1=KF1=SJB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=KF1=SJB2 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1680 | =H1=KF1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=KF1=SJB1 | =L1=JL3+1 | /C120/BC110/SECONDARY
Cable_Id_1681 | =H1=KF1=SJB5=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=KF1=SJB3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1682 | =H1=SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H1=SJB5 | =L1=JL3+1 | /C120/C119/C118/SECONDARY
Cable_Id_1683 | =F2=KF4=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LS =F2=KF4=BLB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170
Cable_Id_1684 | =F2=KF3=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LS =F2=KF3=BLB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/BC169
Cable_Id_1685 | =F1=JF1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F1=JF1=BPA1.2 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1686 | =F1=JF1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F1=JF1=BPA1.1 | =L5=JL1+2 | /BC012/C116/BC013/SECONDARY
Cable_Id_1687 | =H8=JF1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H8=JF1=BPA1 | =L5=JL3+1 | /BC019-2/C138-3/C139/C140/C140/SECONDARY
Cable_Id_1688 | =L7=XDC1=WBA1 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L1=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005
Cable_Id_1689 | =L7=XDC1=WBA2 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L1=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005
Cable_Id_1690 | =L7=XDC1=WBA3 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L2=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001
Cable_Id_1691 | =L7=XDC1=WBA4 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L2=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001
Cable_Id_1692 | =L7=XDC1=WBA5 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L3=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001
Cable_Id_1693 | =L7=XDC1=WBA6 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L3=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001
Cable_Id_1694 | =L7=XDC1=WBA7 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L4=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001/DFC002
Cable_Id_1695 | =L7=XDC1=WBA8 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L4=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006/DFC005/DFC001/DFC002
Cable_Id_1696 | =L7=XDC1=WBA9 | RE-2X(St)H 1x2x0.75mm² | LOCAL CONTROL ROOM=L7=XDC1-X1 | =L5=LC1X7-FDI-X7-FDI | /BC002/BC001/DFC006
Cable_Id_1697 | =H9=JG2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H9=JG2=BFA2 | =L5=JL3+2 | /SECONDARY
Cable_Id_1698 | =H9=KF3=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF3=BPA2 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1699 | =H9=KF3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF3=BPA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1700 | =H9=KF3=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF3=BPA3 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1701 | =H9=KF2=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF2=BPA2 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1702 | =H9=KF2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF2=BPA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1703 | =H9=KF2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF2=BPA3 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1704 | =H9=KF1=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF1=BPA3 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1705 | =H9=KF1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF1=BPA2 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1706 | =H9=KF1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H9=KF1=BPA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1707 | =F1=HD1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =F1=HD1=BPA2 | =L5=JL1+1 | /BC011/C116/BC012/SECONDARY
Cable_Id_1708 | =F2=KF1=GQA1=XDC2=WGA8 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1709 | =H2=HA3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA3=BPC1 | =L1=JL3+2 | /C125/BC124/BC122
Cable_Id_1710 | =F2=QC2=BLB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC2=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2/BC161
Cable_Id_1711 | =F2=QC1=BLB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC1=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2
Cable_Id_1712 | =F2=KF1=GQA1=XDC2=WDB1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1713 | =F2=KF1=GQA1=XDC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1714 | =F2=KF1=GQA1=XDC2=WDB2 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1715 | =F2=KF1=GQA1=XDC2=WGA3 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1716 | =F2=KF1=GQA1=XDC2=WDB3 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1717 | =F2=KF1=GQA1=XDC2=WGA7 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1718 | =F2=KF1=GQA1=XDC2=WGA6 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1719 | =F2=KF1=GQA1=XDC2=WGA4 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1720 | =F2=KF1=GQA1=XDC2=WGA5 | RE-2X(St)H 1x2x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1721 | =F2=KF1=GQA1=XDC2=WGA9 | RE-2X(St)H 1x3x0.75mm² | =F2=KF1=GQA1=XDC2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1722 | =F2=KF2=GQA1=XDC2=WGA8 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1723 | =F2=KF2=GQA1=XDC2=WGA9 | RE-2X(St)H 1x3x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1724 | =F2=KF1=GQA1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB1 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1725 | =F2=KF1=GQA1=BLB2=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB2 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1726 | =F2=KF1=GQA1=BLB3=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF1=GQA1=BLB3 | =F2=KF1=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1727 | =F2=KF2=GQA1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB1 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1728 | =F2=KF2=GQA1=BLB2=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB2 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1729 | =F2=KF2=GQA1=BLB3=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=KF2=GQA1=BLB3 | =F2=KF2=GQA1=XDC2-X1 | /INTERNAL
Cable_Id_1730 | =H9=KF1=GPB1=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF1=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1731 | =H9=KF1=GPB1=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF1=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1732 | =H9=KF1=GPB1=XDC1=WGA4 | RE-2X(St)H 1x2x0.75mm² | =H9=KF1=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1733 | =H9=KF1=GPB1=XDC1=WGA3 | RE-2X(St)H 1x2x0.75mm² | =H9=KF1=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016
Cable_Id_1734 | =H9=KF2=GPB1=XDC1=WGA3 | RE-2X(St)H 1x2x0.75mm² | =H9=KF2=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1735 | =H9=KF2=GPB1=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF2=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1736 | =H9=KF2=GPB1=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF2=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1737 | =H9=KF2=GPB1=XDC1=WGA4 | RE-2X(St)H 1x2x0.75mm² | =H9=KF2=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017
Cable_Id_1738 | =H9=KF3=GPB1=XDC1=WGA3 | RE-2X(St)H 1x2x0.75mm² | =H9=KF3=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1739 | =H9=KF3=GPB1=XDC1=WGA2 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF3=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1740 | =H9=KF3=GPB1=XDC1=WGA1 | RE-2X(St)H TiMF 5x3x0.75mm² | =H9=KF3=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1741 | =H9=KF3=GPB1=XDC1=WGA4 | RE-2X(St)H 1x2x0.75mm² | =H9=KF3=GPB1=XDC1-X1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018
Cable_Id_1742 | =H9=JG2=BHA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | JQI =H9=JG2=BHA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1
Cable_Id_1743 | =H9=JG2=BHA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | JQI =H9=JG2=BHA1 | =L5=JL1+2 | /BC012/C116/C010/C009/BC014/BC016/BC017/BC018/BC028-1/BC028-2
Cable_Id_1744 | =H1=HC1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =H1=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1745 | =F2=KF3=GPB1=BTA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | TE/TT =F2=KF3=GPB1=BTA2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/BC169
Cable_Id_1746 | =F2=KF4=GPB1=BTA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | TE/TT =F2=KF4=GPB1=BTA2 | =L5=JL2+1 | /BC166-1/BC004/BC003/C004/C005/C011/C141/C142/BC170
Cable_Id_1747 | =H1=LC1=XDC2=WGA3 | RE-2X(St)H TiMF 5x3x0.75mm² | =H1=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1748 | =H1=LC1=XDC2=WGA4 | RE-2X(St)H TiMF 5x3x0.75mm² | =H1=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1749 | =H1=LC1=XDC2=WGA5 | RE-2X(St)H TiMF 5x3x0.75mm² | =H1=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1750 | =H1=LC1=XDC2=WGA6 | RE-2X(St)H TiMF 5x3x0.75mm² | =H1=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1751 | =H9=KF3=GPB1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF3=GPB1=BTA1.2=WGA1 |  | /INTERNAL
Cable_Id_1752 | =H9=KF3=GPB1=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF3=GPB1=BTA2.2=WGA1 |  | /INTERNAL
Cable_Id_1753 | =H9=KF3=GPB1=BTA3.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF3=GPB1=BTA3.2=WGA1 |  | /INTERNAL
Cable_Id_1754 | =H9=KF3=GPB1=BTA4.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF3=GPB1=BTA4.2=WGA1 |  | /INTERNAL
Cable_Id_1755 | =H9=KF3=GPB1=BTA5.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF3=GPB1=BTA5.2=WGA1 |  | /INTERNAL
Cable_Id_1756 | =H9=KF2=GPB1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF2=GPB1=BTA1.2=WGA1 |  | /INTERNAL
Cable_Id_1757 | =H9=KF2=GPB1=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF2=GPB1=BTA2.2=WGA1 |  | /INTERNAL
Cable_Id_1758 | =H9=KF2=GPB1=BTA3.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF2=GPB1=BTA3.3=WGA1 |  | /INTERNAL
Cable_Id_1759 | =H9=KF2=GPB1=BTA4.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF2=GPB1=BTA4.2=WGA1 |  | /INTERNAL
Cable_Id_1760 | =H9=KF2=GPB1=BTA5.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF2=GPB1=BTA5.2=WGA1 |  | /INTERNAL
Cable_Id_1761 | =H9=KF1=GPB1=BTA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | B1-=H9=KF1=GPB1=BTA1.2=WGA1 |  | /INTERNAL
Cable_Id_1762 | =H9=KF1=GPB1=BTA2.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | B1-=H9=KF1=GPB1=BTA2.2=WGA1 |  | /INTERNAL
Cable_Id_1763 | =H9=KF1=GPB1=BTA3.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF1=GPB1=BTA3.2=WGA1 |  | /INTERNAL
Cable_Id_1764 | =H9=KF1=GPB1=BTA4.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF1=GPB1=BTA4.2=WGA1 |  | /INTERNAL
Cable_Id_1765 | =H9=KF1=GPB1=BTA5.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-=H9=KF1=GPB1=BTA5.2=WGA1 |  | /INTERNAL
Cable_Id_1766 | =H2=LC1=XDC1=WGA1 | Li02YCHXSHX[BK] 18x4 x 0.50mm² | =H2=LC1=XDC1-XT | =H2=LC1=UCA1-125XT......130XT | /DFC004-1/DFC003/C002/C107-1/C108/C123/C124/C125/C126/C127
Cable_Id_1767 | =H2=JF1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF1=BPA1.1 | =L1=JL1+1 | /BC121/BC122/SECONDARY
Cable_Id_1768 | =F2=KF2=GQA1=XDC2=WGA5 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1769 | =F2=KF2=GQA1=XDC2=WDB3 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1770 | =F2=KF2=GQA1=XDC2=WGA6 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1771 | =F2=KF2=GQA1=XDC2=WGA4 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1772 | =F2=KF2=GQA1=XDC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1773 | =F2=KF2=GQA1=XDC2=WDB2 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1774 | =F2=KF2=GQA1=XDC2=WGA7 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1775 | =F2=KF2=GQA1=XDC2=WGA3 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1776 | =F2=KF2=GQA1=XDC2=WGA2 | RE-2X(St)H 1x2x0.75mm² | =F2=KF2=GQA1=XDC2 | =L5=JL2+2 | /BC166-2/BC160-1/C145/C144/C004/C005/C011/C141/C142/BC170/SECONDARY
Cable_Id_1777 | =F2=QC3=BLB2=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC3=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/BC171/BC163/SECONDARY
Cable_Id_1778 | =F2=QC3=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC3=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC162/SECONDARY
Cable_Id_1779 | =F2=QC2=BLB2=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC2=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/BC172/BC164/SECONDARY
Cable_Id_1780 | =F2=QC2=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC2=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/BC161/SECONDARY
Cable_Id_1781 | =F2=QC1=BLB2=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSH =F2=QC1=BLB2 | =L5=JL2+1 | /BC166-1/BC160-2/BC173/BC165/SECONDARY
Cable_Id_1782 | =F2=QC1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =F2=QC1=BLB1 | =L5=JL2+1 | /BC166-1/BC160-2/SECONDARY
Cable_Id_1783 | =H2=LC1=XDC2=WGA2 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H2=LC1=XDC2-SMX7/1 | =H2=LC1=UCA1-121 SMX7/1 | /DFC004-1/DFC003/C002/C107-1/C108/C123/C124/C125/C126/C127
Cable_Id_1784 | =H2=LC1=XDC2=WGA1 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H2=LC1=XDC2-SMX7/2 | =H2=LC1=UCA1-122 SMX7/2 | /DFC004-1/DFC003/C002/C107-1/C108/C123/C124/C125/C126/C127
Cable_Id_1785 | =H2=LC1=XDC1=WDB2 | HXSLCHXSHX 12 x 6mm² | =H2=LC1=UCA1-105XPA | =H2=LC1=XDC1-XPA | /DFB018-1/DFB027/B007/B139-1/B108/B120/B121
Cable_Id_1786 | =H2=LC1=XDC1=WGA2 | RE-2X(St)H 1x3x0.75mm² | =H2=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1787 | =H2=LC1=XDC1=WGA3 | RE-2X(St)H 1x3x0.75mm² | =H2=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1788 | =H2=LC1=XDC1=WDB4 | HXSLCHXSHX 12 x 6mm² | =H2=LC1=UCA1-105XPM | =H2=LC1=XDC1-XPM | /DFB018-1/DFB027/B007/B139-1/B108/B120/B121
Cable_Id_1789 | =H2=LC1=XDC2=WGA7 | RE-2X(St)H 1x3x0.75mm² | =H2=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1790 | =H2=LC1=XDC2=WGA8 | RE-2X(St)H 1x3x0.75mm² | =H2=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1791 | =H2=LC1=XDC1=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H2=LC1=XDC1-XG | /SECONDARY
Cable_Id_1792 | =H2=LC1=XDC1=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H2=LC1=XDC1-XG | /SECONDARY
Cable_Id_1793 | =H2=LC1=XDC2=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H2=LC1=XDC2-XG | /SECONDARY
Cable_Id_1794 | =H2=LC1=XDC2=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H2=LC1=XDC2-XG | /SECONDARY
Cable_Id_1795 | =H2=LC1=XDC1=BTA1=WGA1 | JZ-600 3G 1.5MM² | TSHL =H2=LC1=XDC1=BTA1 | =H2=LC1=XDC1-XPH | /SECONDARY
Cable_Id_1796 | =H2=LC1=XDC2=BTA2=WGA1 | JZ-600 3G 1.5MM² | TSHL =H2=LC1=XDC2=BTA2 | =H2=LC1=XDC2-XPH | /SECONDARY
Cable_Id_1797 | =H2=LC1=XDC1=WDB3 | HXSLCHXSHX 12 x 6mm² | =H2=LC1=XDC1-XPC | =H2=LC1=UCA1-105XPC | /DFB018-1/DFB027/B007/B139-1/B108/B120/B121
Cable_Id_1798 | =H2=HA2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA2=BTA2.3 | TIT =H2=HA2=BTA2.3 | /SECONDARY
Cable_Id_1799 | =H2=HA2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA2=BTA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1800 | =H2=HA2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA2=BTA2.2 | TIT =H2=HA2=BTA2.2 | /SECONDARY
Cable_Id_1801 | =H2=HA2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA2=BTA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_1802 | =H2=HA2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA2=BTA2.1 | TIT =H2=HA2=BTA2.1 | /SECONDARY
Cable_Id_1803 | =H2=HA2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA2=BTA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_1804 | =H2=HA2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA2=BTA1 | TIT =H2=HA2=BTA1 | /SECONDARY
Cable_Id_1805 | =H2=HA2=BPA2.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA2=BPA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1806 | =H2=HA2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA2=BPA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_1807 | =H2=HA2=BPA2.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA2=BPA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_1808 | =H2=HA2=BPA2.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA2=BPA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_1809 | =H2=HA2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=HA2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1810 | =H2=HA3=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA3=BTA1.2 | TIT =H2=HA3=BTA1.2 | /SECONDARY
Cable_Id_1811 | =H2=HA3=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA3=BTA1.1 | TIT =H2=HA3=BTA1.1 | /SECONDARY
Cable_Id_1812 | =H2=HA1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA1=BTA1.2 | TIT =H2=HA1=BTA1.2 | /SECONDARY
Cable_Id_1813 | =H2=HA1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA1=BTA1.1 | TIT =H2=HA1=BTA1.1 | /SECONDARY
Cable_Id_1814 | =H2=HA4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA4=BTA1 | TIT =H2=HA4=BTA1 | /SECONDARY
Cable_Id_1815 | =H2=HA4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA4=BTA2 | TIT =H2=HA4=BTA2 | /SECONDARY
Cable_Id_1816 | =H2=HA1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA1=BTA2 | TIT =H2=HA1=BTA2 | /SECONDARY
Cable_Id_1817 | =H2=HA5=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA5=BTA1 | TIT =H2=HA5=BTA1 | /SECONDARY/BC128/BC120/SECONDARY
Cable_Id_1818 | =H2=HA2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA2=BPC1 | =L1=JL3+1 | /C125/C124/C123/SECONDARY
Cable_Id_1819 | =H2=HA2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA2=BPA3 | =L1=JL3+2 | /C125/C124/C123/SECONDARY
Cable_Id_1820 | =H2=HA2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA2=BPC2 | =L1=JL3+2 | /C125/C124/C123/SECONDARY
Cable_Id_1821 | =H2=HA3=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA3=BTA1.2 | =L1=JL3+1 | /C125/C124/C123/SECONDARY
Cable_Id_1822 | =H2=HA3=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA3=BTA1.1 | =L1=JL3+1 | /C125/C124/C123/SECONDARY
Cable_Id_1823 | =H2=HA3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA3=BPA1 | =L1=JL3+2 | /SECONDARY/BC123/BC122/BC124/C125
Cable_Id_1824 | =H2=HA1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA1=BTA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1825 | =H2=HA1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA1=BTA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1826 | =H2=HA1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA1=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_1827 | =H2=HA1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA1=BPC2 | =L1=JL1+1 | /SECONDARY/BC123/BC122/BC121
Cable_Id_1828 | =H2=HA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA1=BPA1.2 | =L1=JL2+1 | /SECONDARY/BC121/BC120/C127
Cable_Id_1829 | =H2=HA1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA1=BPA2 | =L1=JL2+2 | /SECONDARY/BC121/BC120/C127
Cable_Id_1830 | =H2=HA4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA4=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1831 | =H2=HA4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA4=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_1832 | =H2=HA4=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA4=BPA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1833 | =H2=HA4=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA4=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1834 | =H2=HA4=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA4=BPA2 | =L1=JL1+2 | /SECONDARY/BC120/BC121
Cable_Id_1835 | =H2=HA5=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA5=BTA1 | =L1=JL2+2 | /SECONDARY/BC120/C127
Cable_Id_1836 | =H2=HA5=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA5=BPA1 | =L1=JL2+2 | /SECONDARY/BC120/C127
Cable_Id_1837 | =H2=HA5=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA5=BPA2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1838 | =H2=HA5=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA5=BPC1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1839 | =H2=KF1=GQB1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FT =H2=KF1=GQB1=BFA1 | =L1=JL1+2 | /SECONDARY/BC128/BC127/BC121
Cable_Id_1840 | =H2=HA2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1841 | =H2=HA2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA2=QNB1 | =L1=JL3+1 | /C125/C126/C127/BC120/BC128
Cable_Id_1842 | =H2=HA4=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA4=QNB1 | =L1=JL1+2 | /BC121/BC127/SECONDARY
Cable_Id_1843 | =H2=HA4=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA4=QNB1 | =L1=JL1+1 | /BC121/BC127/SECONDARY
Cable_Id_1844 | =H2=HA4=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=HA4=QNB1 | =L1=JL1+2 | /BC121/BC127/SECONDARY
Cable_Id_1845 | =H2=HA5=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA5=QNB1 | =L1=JL2+2 | /C127/BC120/BC128/SECONDARY
Cable_Id_1846 | =H2=HA5=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA5=QNB1 | =L1=JL2+1 | /C127/BC120/BC128/SECONDARY
Cable_Id_1847 | =H2=HA2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA2=BTA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_1848 | =H2=HA5=QNB1=WGA3 | RE-2X(St)H PiMF 2x2x0.75mm² | PY =H2=HA5=QNB1 | =L1=JL2+2 | /C127/BC120/BC128/SECONDARY
Cable_Id_1849 | =H2=HA1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HA1=BPC1 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1850 | =H2=HA7=BTA1.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA7=BTA1.3 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1851 | =H2=HA7=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA7=BTA1.2 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1852 | =H2=HA7=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HA7=BTA1.1 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1853 | =H2=HA7=BTA1.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA7=BTA1.3 | TIT =H2=HA7=BTA1.3 | /SECONDARY
Cable_Id_1854 | =H2=HA7=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA7=BTA1.2 | TIT =H2=HA7=BTA1.2 | /SECONDARY
Cable_Id_1855 | =H2=HA7=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HA7=BTA1.1 | TIT =H2=HA7=BTA1.1 | /SECONDARY
Cable_Id_1856 | =H3=LC1=XDC1=BQB1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H3=LC1=XDC1-XG | /SECONDARY
Cable_Id_1857 | =H2=JF1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF1=BPA1.2 | =L1=JL1+1 | /BC121/BC122/SECONDARY
Cable_Id_1858 | =H2=JF2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF2=BPA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1859 | =H2=JF2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF2=BPA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1860 | =H2=JF1=BPC1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JF1=BPC1.1 | =L1=JL2+1 | /C127/BC120/BC128/BC127/BC121/BC122/SECONDARY
Cable_Id_1861 | =H2=JF1=BPC1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JF1=BPC1.2 | =L1=JL2+1 | /C127/BC120/BC128/BC127/BC121/BC122/SECONDARY
Cable_Id_1862 | =H2=HC1=BLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LIT =H2=HC1=BLA1 | =L1=JL1+2 | /BC121/BC122/SECONDARY
Cable_Id_1863 | =H2=HC1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HC1=BPA1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/SECONDARY
Cable_Id_1864 | =H2=HC1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HC1=BTA1.1 | =L1=JL2+1 | /C127/BC120/BC128/BC127/BC121/BC122/SECONDARY
Cable_Id_1865 | =H2=HC1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HC1=BTA1.2 | =L1=JL2+1 | /C127/BC120/BC128/BC127/BC121/BC122/SECONDARY
Cable_Id_1866 | =H2=HC1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HC1=BTA1.2 | TIT =H2=HC1=BTA1.2 | /SECONDARY
Cable_Id_1867 | =H2=HC1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HC1=BTA1.1 | TIT =H2=HC1=BTA1.1 | /SECONDARY
Cable_Id_1868 | =H2=HE1=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HE1=BPA1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1869 | =H2=JF2=BTA2.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF2=BTA2.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_1870 | =H2=JF2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF2=BTA1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1871 | =H2=JF2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF2=BTA1 | TIT =H2=JF2=BTA1 | /BC120/SECONDARY
Cable_Id_1872 | =H2=JF2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF2=BTA2.1 | TIT =H2=JF2=BTA2.1 | /SECONDARY
Cable_Id_1873 | =H2=JF2=BQC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | AIT =H2=JF2=BQC1 | =L1=JL1+2 | /BC121/BC120/C127
Cable_Id_1874 | =H2=JF2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H2=JF2=BFB1 | =L1=JL1+2 | /BC121/BC120/C127
Cable_Id_1875 | =H2=JF2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=JF2=BFA1 | =L1=JL1+1 | /BC121/BC120/C127
Cable_Id_1876 | =H2=KC1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=KC1=BPC1 | =H2=KC1=UCA1X1-AI-X1-AI | /SECONDARY
Cable_Id_1877 | =H2=JG2=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JG2=BPA1.1 | =L1=JL3+1 | /C125/BC124/BC122/BC123/SECONDARY
Cable_Id_1878 | =H2=JG2=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JG2=BPA1.2 | =L1=JL3+1 | /C125/BC124/BC122/BC123/SECONDARY
Cable_Id_1879 | =H2=JG2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JG2=BTA1 | =L1=JL3+2 | /C125/BC124/SECONDARY
Cable_Id_1880 | =H2=JG2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JG2=BTA1 | TIT =H2=JG2=BTA1 | /SECONDARY/BC122/BC123/SECONDARY
Cable_Id_1881 | =H2=JG2=BQC1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | UT =H2=JG2=BQC1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1882 | =H2=JG2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JG2=BPC1 | =L1=JL3+2 | /C125/C124/C123/SECONDARY
Cable_Id_1883 | =H2=JG2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JG2=BPC2 | =L1=JL3+2 | /C125/BC124/BC122/BC123/SECONDARY
Cable_Id_1884 | =H2=JG2=BFB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FSL =H2=JG2=BFB1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1885 | =H2=JG2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JG2=QNA1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1886 | =H2=JG2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=JG2=QNA1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1887 | =H2=JG1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JG1=BPA1.2 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1888 | =H2=JG1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JG1=BPA1.1 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1889 | =H2=JG1=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JG1=BPC1 | =L1=JL3+2 | /C125/BC124/SECONDARY
Cable_Id_1890 | =H2=JG1=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=JG1=BFA1 | =L1=JL1+2 | /BC121/BC122/SECONDARY
Cable_Id_1891 | =H2=JG1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JG1=BPA2 | =L1=JL3+2 | /C125/BC124/SECONDARY
Cable_Id_1892 | =H2=JG1=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JG1=BTA1 | =L1=JL3+2 | /C125/C124/C123/SECONDARY
Cable_Id_1893 | =H2=JG1=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JG1=BTA1 | TIT =H2=JG1=BTA1 | /SECONDARY
Cable_Id_1894 | =H2=JF3=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF3=BTA1 | TIT =H2=JF3=BTA1 | /SECONDARY
Cable_Id_1895 | =H2=JF3=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF3=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1896 | =H2=JF3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF3=BPA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1897 | =H2=JF3=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=JF3=BPA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1898 | =H2=JF3=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JF3=BPC2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1899 | =H2=JF3=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=JF3=BPC1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1900 | =H2=JF3=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=JF3=BFA1 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1901 | =H2=JF4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF4=BTA1 | TIT =H2=JF4=BTA1 | /SECONDARY
Cable_Id_1902 | =H2=JF4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF4=BTA2 | TIT =H2=JF4=BTA2 | /BC031/BC030/BC029/SECONDARY
Cable_Id_1903 | =H2=JF4=BTA3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF4=BTA3 | TIT =H2=JF4=BTA3 | /BC031/BC030/BC029/SECONDARY
Cable_Id_1904 | =H2=JF4=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF4=BTA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1905 | =H2=JF4=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF4=BTA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1906 | =H2=JF4=BTA3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF4=BTA3 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1907 | =H2=JF4=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF4=QNA1 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1908 | =H2=JF4=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1909 | =H2=JF4=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1910 | =H2=JF4=QNA2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1911 | =H2=JF4=QNA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF4=QNA2 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1912 | =H2=JF4=QNA2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1913 | =H2=JF2=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF2=QMA10 | =L1=JL2+2 | /C127/BC120
Cable_Id_1914 | =H2=HC2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H2=HC2=BPC1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1915 | =H2=HC2=BFA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=HC2=BFA3 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1916 | =H2=HC2=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=HC2=BFA1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1917 | =H2=HC2=BFA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=HC2=BFA4 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1918 | =H2=HC2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=HC2=BTA1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1919 | =H2=HC2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=HC2=BTA1 | TIT =H2=HC2=BTA1 | /SECONDARY
Cable_Id_1920 | =H2=HC2=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=HC2=BFA2 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1921 | =H2=HC2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=HC2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1922 | =H2=HC2=QNB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HC2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1923 | =H2=HC2=QNB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HC2=QNB1 | =L1=JL3+1 | /C125/C126/C127/BC120/BC128
Cable_Id_1924 | =H2=KF1=MAA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=KF1=MAA1=BPA1.1 | =L1=JL3+1 | /C125/C126/SECONDARY
Cable_Id_1925 | =H2=KF1=MAA1=BPA1.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=KF1=MAA1=BPA1.3 | =L1=JL3+1 | /C125/C126/SECONDARY
Cable_Id_1926 | =H2=KF1=MAA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=KF1=MAA1=BPA1.2 | =L1=JL3+1 | /C125/C126/SECONDARY
Cable_Id_1927 | =H2=KF1=PZA1=WGA1 | RE-2X(St)H PiMF 2x2x0.75mm² | XI =H2=KF1=PZA1 | =L1=JL3+2 | /C125/BC124/SECONDARY
Cable_Id_1928 | =H2=HA5=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA5=QMB1 | =L1=JL2+1 | /C127/BC120/BC128/SECONDARY
Cable_Id_1929 | =H2=HA5=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA5=QMB1 | =L1=JL2+1 | /C127/BC120/BC128/SECONDARY
Cable_Id_1930 | =H2=HA2=FLA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA2=FLA1 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1931 | =H2=HA2=FLA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA2=FLA1 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1932 | =H2=HA7=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106/C107-1/C108/C123/C124/BC124/BC122/BC123/SECONDARY
Cable_Id_1933 | =H2=HA7=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA7=QMB1 | =L5=JL2+1 | /BC166-1/BC004/BC003/C105-2/C105-1/C104/C102/C101/C106/C107-1/C108/C123/C124/BC124/BC122/BC123/SECONDARY
Cable_Id_1934 | =H2=JF2=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H2=JF2=BLB1 | =L1=JL2+2
Cable_Id_1935 | =H2=JF1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSH =H2=JF1=BLB1 | =L1=JL1+2
Cable_Id_1936 | =H2=HC1=QMA4=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_1937 | =H2=HC1=QMA4=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HC1=QMA4 | =L1=JL1+1 | /SECONDARY
Cable_Id_1938 | =H2=HA1=BPA1.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H2=HA1=BPA1.1 | =L1=JL2+1 | /C127/BC120/BC121/SECONDARY
Cable_Id_1939 | =H2=JF1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF1=QMB1 | =L1=JL1+2 | /BC121/BC120/SECONDARY
Cable_Id_1940 | =H2=JF1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF1=QMB1 | =L1=JL1+2 | /BC121/BC120/SECONDARY
Cable_Id_1941 | =H2=HC2=QNB2=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HC2=QNB2 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128/SECONDARY
Cable_Id_1942 | =H2=HC2=QNB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HC2=QNB2 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128/SECONDARY
Cable_Id_1943 | =H2=HA2=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=HA2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1944 | =H2=HA5=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=HA5=QNB1 | =L1=JL2+2 | /C127/BC120/BC128/SECONDARY
Cable_Id_1945 | =H2=HA4=QNB1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=HA4=QNB1 | =L1=JL1+2 | /BC121/BC127/SECONDARY
Cable_Id_1946 | =H2=HC2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=HC2=QNB1 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128
Cable_Id_1947 | =H2=JG2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=JG2=QNA1 | =L1=JL2+2 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1948 | =H2=JF4=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=JF4=QNA1 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1949 | =H2=JF4=QNA2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=JF4=QNA2 | =L5=JL3+2 | /BC019-1/C138-1/C143-5/C143-4/BC025/BC022-1/SECONDARY
Cable_Id_1950 | =H2=JF3=BFA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=JF3=BFA2 | =L5=JL3+1 | /BC019-1/C138-1/C143-5/C143-4/C143-3/BC175/BC030/BC029/SECONDARY
Cable_Id_1951 | =H2=HA1=QMB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HA1=QMB1 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1952 | =H2=HA1=QMB1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HA1=QMB1 | =L1=JL1+1 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1953 | =H2=HE1=QMA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=HE1=QMA1 | =L1=JL1+1 | /BC121/SECONDARY
Cable_Id_1954 | =H2=HE1=QMA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=HE1=QMA1 | =L1=JL1+1 | /BC121/SECONDARY
Cable_Id_1955 | =H2=HC2=QNB2=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=HC2=QNB2 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128/SECONDARY
Cable_Id_1956 | =H2=JF2=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF2=QMA10 | =L1=JL2+2 | /C127/BC120
Cable_Id_1957 | =H2=JG2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JG2=QNA1 | =L1=JL2+1 | /C127/BC120/BC128/BC127/BC121/BC122/BC123/SECONDARY
Cable_Id_1958 | =H2=HC2=QNB2=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=HC2=QNB2 | =L1=JL3+2 | /C125/C126/C127/BC120/BC128/SECONDARY
Cable_Id_1959 | =H2=HC1=BLB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | LSL =H2=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1960 | =H2=JF1=QMA10=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF1=QMA10 | =L1=JL1+2 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1961 | =H2=JF1=QMA10=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF1=QMA10 | =L1=JL1+2 | /BC121/BC122/BC123/SECONDARY
Cable_Id_1962 | =H2=JF2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF2=BTA2.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_1963 | =H2=JF2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF2=BTA2.2 | TIT =H2=JF2=BTA2.2 | /SECONDARY
Cable_Id_1964 | =H2=JF2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H2=JF2=BTA2.3 | =L1=JL1+1 | /SECONDARY
Cable_Id_1965 | =H2=JF2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H2=JF2=BTA2.3 | TIT =H2=JF2=BTA2.3 | /SECONDARY
Cable_Id_1966 | =H2=JF2=QNA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF2=QNA1 | =L1=JL3+2 | /C125/C126/SECONDARY
Cable_Id_1967 | =H2=JF2=QNA1=WGA2 | RE-2X(St)H PiMF 2x2x0.75mm² | ZSO =H2=JF2=QNA1 | =L1=JL3+2 | /C125/C126/SECONDARY
Cable_Id_1968 | =H2=JF2=QNA1=WGA4 | RE-2X(St)H 1x2x0.75mm² | ZT =H2=JF2=QNA1 | =L1=JL3+2 | /C125/C126/SECONDARY
Cable_Id_1969 | =H2=JF2=QNA1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H2=JF2=QNA1 | =L1=JL3+2 | /BC121/BC120/C127
Cable_Id_1970 | =H2=JF2=QMA6=WGA1 | RE-2X(St)H 1x2x0.75mm² | XV =H2=JF2=QMA6 | =L1=JL1+2 | /SECONDARY
Cable_Id_1971 | =H2=HA4=BFA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | FIT =H2=HA4=BFA1 | =L1=JL1+2 | /C127/BC120/BC128/SECONDARY
Cable_Id_1972 | =H2=SJB3=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=SJB6 | =L1=JL1+1 | /C125/BC124/BC123/SECONDARY
Cable_Id_1973 | =H2=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=SJB4 | =L1=JL2+1 | /C125/C126/SECONDARY
Cable_Id_1974 | =H2=KF1=SJB4=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=KF1=SJB2 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1975 | =H2=KF1=SJB1=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=KF1=SJB1 | =L1=JL3+1 | /C125/BC124/SECONDARY
Cable_Id_1976 | =H2=KF1=SJB5=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=KF1=SJB3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1977 | =H2=SJB2=WGA1 | RE-2X(St)H 1x2x0.75mm² | HS =H2=SJB5 | =L1=JL3+1 | /C125/C124/C123/SECONDARY
Cable_Id_1978 | =H2=HC1=BLB1=WDB1 | RE-2X(St)H 1x2x0.75mm² | LSL =H2=HC1=BLB1 | =L1=JL1+2 | /SECONDARY
Cable_Id_1979 | =H2=LC1=XDC2=WGA3 | RE-2X(St)H TiMF 5x3x0.75mm² | =H2=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1980 | =H2=LC1=XDC2=WGA4 | RE-2X(St)H TiMF 5x3x0.75mm² | =H2=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1981 | =H2=LC1=XDC2=WGA5 | RE-2X(St)H TiMF 5x3x0.75mm² | =H2=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1982 | =H2=LC1=XDC2=WGA6 | RE-2X(St)H TiMF 5x3x0.75mm² | =H2=LC1=XDC2-XS11 | =L1=JL2+1 | /SECONDARY
Cable_Id_1983 | =H3=LC1=XDC1=WGA1 | Li02YCHXSHX[BK] 18x4 x 0.50mm² | =H3=LC1=XDC1-XT | =H3=LC1=UCA1-125XT......130XT | /DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/C130/C131/C132
Cable_Id_1984 | =H3=LC1=XDC2=WGA2 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H3=LC1=XDC2-SMX7/1 | =H3=LC1=UCA1-121 SMX7/1 | /DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/C130/C131/C132
Cable_Id_1985 | =H3=LC1=XDC2=WGA1 | Li02YCHXSHX[BK] 8x2x 0.25mm² | =H3=LC1=XDC2-SMX7/2 | =H3=LC1=UCA1-122 SMX7/2 | /DFC003/C002/C107-1/C107-2/C107-3/C107-4/C107-5/C107-6/C107-7/C111/C128/C129/C130/C131/C132
Cable_Id_1986 | =H3=LC1=XDC1=WDB2 | HXSLCHXSHX 12 x 6mm² | =H3=LC1=UCA1-105XPA | =H3=LC1=XDC1-XPA | /DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B111/B122/B123
Cable_Id_1987 | =H3=LC1=XDC1=WGA2 | RE-2X(St)H 1x3x0.75mm² | =H3=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1988 | =H3=LC1=XDC1=WGA3 | RE-2X(St)H 1x3x0.75mm² | =H3=LC1=XDC1-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1989 | =H3=LC1=XDC1=WDB4 | HXSLCHXSHX 12 x 6mm² | =H3=LC1=UCA1-105XPM | =H3=LC1=XDC1-XPM | /DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B111/B122/B123
Cable_Id_1990 | =H3=LC1=XDC2=WGA7 | RE-2X(St)H 1x3x0.75mm² | =H3=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1991 | =H3=LC1=XDC2=WGA8 | RE-2X(St)H 1x3x0.75mm² | =H3=LC1=XDC2-XG | =L1=JL2+1 | /SECONDARY
Cable_Id_1992 | =H3=LC1=XDC1=BQB1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | B1-X | =H3=LC1=XDC1-XG | /SECONDARY
Cable_Id_1993 | =H3=LC1=XDC1=BTA1=WGA1 | JZ-600 3G 1.5MM² | TSHL =H3=LC1=XDC1=BTA1 | =H3=LC1=XDC1-XPH | /SECONDARY
Cable_Id_1994 | =H3=LC1=XDC2=BTA2=WGA1 | JZ-600 3G 1.5MM² | TSHL =H3=LC1=XDC2=BTA2 | =H3=LC1=XDC2-XPH | /SECONDARY
Cable_Id_1995 | =H3=LC1=XDC1=WDB3 | HXSLCHXSHX 12 x 6mm² | =H3=LC1=XDC1-XPC | =H3=LC1=UCA1-105XPC | /DFB027/B007/B139-1/B139-2/B139-3/B139-4/B139-5/BC180/BC181/B111/B122/B123
Cable_Id_1996 | =H3=HA2=BTA2.3=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA2=BTA2.3 | TIT =H3=HA2=BTA2.3 | /SECONDARY
Cable_Id_1997 | =H3=HA2=BTA2.3=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA2=BTA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_1998 | =H3=HA2=BTA2.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA2=BTA2.2 | TIT =H3=HA2=BTA2.2 | /SECONDARY
Cable_Id_1999 | =H3=HA2=BTA2.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA2=BTA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_2000 | =H3=HA2=BTA2.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA2=BTA2.1 | TIT =H3=HA2=BTA2.1 | /SECONDARY
Cable_Id_2001 | =H3=HA2=BTA1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA2=BTA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_2002 | =H3=HA2=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA2=BTA1 | TIT =H3=HA2=BTA1 | /SECONDARY
Cable_Id_2003 | =H3=HA2=BPA2.3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA2=BPA2.3 | =L1=JL3+1 | /SECONDARY
Cable_Id_2004 | =H3=HA2=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA2=BPA1 | =L1=JL3+2 | /SECONDARY
Cable_Id_2005 | =H3=HA2=BPA2.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA2=BPA2.2 | =L1=JL3+1 | /SECONDARY
Cable_Id_2006 | =H3=HA2=BPA2.1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA2=BPA2.1 | =L1=JL3+1 | /SECONDARY
Cable_Id_2007 | =H3=HA2=QNB1=WGA3 | RE-2X(St)H 1x2x0.75mm² | PY =H3=HA2=QNB1 | =L1=JL3+2 | /C130/C131/C132/BC134/BC142
Cable_Id_2008 | =H3=HA3=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA3=BTA1.2 | TIT =H3=HA3=BTA1.2 | /SECONDARY
Cable_Id_2009 | =H3=HA3=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA3=BTA1.1 | TIT =H3=HA3=BTA1.1 | /SECONDARY
Cable_Id_2010 | =H3=HA1=BTA1.2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA1=BTA1.2 | TIT =H3=HA1=BTA1.2 | /SECONDARY
Cable_Id_2011 | =H3=HA1=BTA1.1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA1=BTA1.1 | TIT =H3=HA1=BTA1.1 | /SECONDARY
Cable_Id_2012 | =H3=HA4=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA4=BTA1 | TIT =H3=HA4=BTA1 | /SECONDARY
Cable_Id_2013 | =H3=HA4=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA4=BTA2 | TIT =H3=HA4=BTA2 | /SECONDARY
Cable_Id_2014 | =H3=HA1=BTA2=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA1=BTA2 | TIT =H3=HA1=BTA2 | /SECONDARY
Cable_Id_2015 | =H3=HA5=BTA1=WGA1 | RE-2X(St)H 1x3x0.75mm² | TE =H3=HA5=BTA1 | TIT =H3=HA5=BTA1 | /SECONDARY/BC142/BC134/SECONDARY
Cable_Id_2016 | =H3=HA2=BPC1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA2=BPC1 | =L1=JL3+1 | /C130/C129/C128/SECONDARY
Cable_Id_2017 | =H3=HA2=BPA3=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA2=BPA3 | =L1=JL3+2 | /C130/C129/C128/SECONDARY
Cable_Id_2018 | =H3=HA2=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA2=BPC2 | =L1=JL3+2 | /C130/C129/C128/SECONDARY
Cable_Id_2019 | =H3=HA3=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA3=BTA1.2 | =L1=JL3+1 | /C130/C129/C128/SECONDARY
Cable_Id_2020 | =H3=HA3=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA3=BTA1.1 | =L1=JL3+1 | /C130/C129/C128/SECONDARY
Cable_Id_2021 | =H3=HA3=BPA1=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA3=BPA1 | =L1=JL3+2 | /SECONDARY/BC137/BC136/BC138/C130
Cable_Id_2022 | =H3=HA1=BTA1.2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA1=BTA1.2 | =L1=JL1+1 | /SECONDARY
Cable_Id_2023 | =H3=HA1=BTA1.1=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA1=BTA1.1 | =L1=JL1+1 | /SECONDARY
Cable_Id_2024 | =H3=HA1=BTA2=WGA2 | RE-2X(St)H 1x2x0.75mm² | TIT =H3=HA1=BTA2 | =L1=JL1+2 | /SECONDARY
Cable_Id_2025 | =H3=HA1=BPC2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PDIT =H3=HA1=BPC2 | =L1=JL1+1 | /SECONDARY/BC137/BC136/BC135
Cable_Id_2026 | =H3=HA1=BPA1.2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA1=BPA1.2 | =L1=JL2+1 | /SECONDARY/BC135/BC134/C132
Cable_Id_2027 | =H3=HA1=BPA2=WGA1 | RE-2X(St)H 1x2x0.75mm² | PIT =H3=HA1=BPA2 | =L1=JL2+2 | /SECONDARY/BC135/BC134/C132